## query (5)
UniqueID | FacNum | Content Type | LoopType | EntryGroup | SurveyDate | Conductivity | TRASAR | pH | ORP | MAlkalinity | TotalHardness | CalciumHardness | Phosphonate | OrthoPhosphate | Polymer | Zinc | Azole | FreeChlorine | Copper | Iron | TotalBacteria | MakeupMeter | BlowdownMeter | WaterMeterCycles | MildSteelCorrosionRate | MildCopperCorrosionRate | MeteringPumpOperation | UnitCondition | Debris | Filters | ChemicalInventory | Notes | DataEntryUser | PumpSpeedAdjustment | StrokeSetting | Temperature | Created | CreatedBy
1 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 10:58 | [26 empty] | ​tower is still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2018-03-16 11:02 | Daimon A. Boccamazzo
2 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 08:49 | [26 empty] | ​tower still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-09-13 08:51 | Daimon A. Boccamazzo
3 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-23 07:29 | [26 empty] | ​tower is still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-26 07:30 | Daimon A. Boccamazzo
4 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-06 10:24 | [26 empty] | ​tower is still offline but has new controller and chemicals ready to go. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-12-12 10:27 | Daimon A. Boccamazzo
5 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-24 14:12 | [26 empty] | ​tower still offline until further notice | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-10-24 14:14 | Daimon A. Boccamazzo
6 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-19 10:24 | [26 empty] | ​tower is still offline, makeup valve shut and drain valve open, tower is dry. New controller and chemicals are there | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-07-20 10:26 | Daimon A. Boccamazzo
7 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:37 | [26 empty] | ​make up water valve is closed and bleed valve is open. Tower is dry. New Nalco controller is hooked up and chemicals are there and ready to be hooked up | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-06-02 13:39 | Daimon A. Boccamazzo
8 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-18 13:10 | [26 empty] | ​chemical are there but not hooked up to the pumps and new Nalco controller is not setup. Closed make up water valve and drained the tower | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-18 13:12 | Daimon A. Boccamazzo
9 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 07:51 | 320 | 0 | 8 | 240 | [8 empty] | 0 | [13 empty] | ​Tower has not been running. | Bob A Adams | Not Adjusted |  | 56.9 | 2016-03-31 07:53 | Bob A Adams
10 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-02 14:30 | 331 | 8 | 8.1 | 318 | [8 empty] | 2 | [13 empty] | ​This a CH2O treatment system wand the test results are within their parameters | mrh4 | Not Adjusted |  |  | 2015-10-02 14:36 | mrh4
11 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-18 10:20 | 498.6 |  |  | 82 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 55 | 2018-10-01 10:21 | RICHARD A. JOHNSON
12 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-24 09:21 | 798.8 |  |  | 134 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2018-07-30 09:22 | RICHARD A. JOHNSON
13 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-18 10:29 | 1077 |  |  | 103 | [8 empty] | 1.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 63 | 2018-05-31 10:29 | RICHARD A. JOHNSON
14 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-26 07:57 | 778 |  |  | 171 | [8 empty] | 4.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 52 | 2018-04-02 07:58 | RICHARD A. JOHNSON
15 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-27 10:51 | 965 |  |  | 202 | [8 empty] | 0.4 | [13 empty] | ​cleaned strainer and flow meter. | Daimon A. Boccamazzo | Not Adjusted |  | 50 | 2018-03-16 10:56 | Daimon A. Boccamazzo
16 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-30 13:23 | 965 |  |  | 136 | [8 empty] | 1.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 51 | 2018-02-01 13:24 | RICHARD A. JOHNSON
17 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-22 12:11 | 740 |  |  | 193 | [8 empty] | 2.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 61 | 2017-12-04 12:13 | RICHARD A. JOHNSON
18 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-30 11:43 | 870 |  |  | 201 | [8 empty] | 1.9 | [13 empty] | ​cleaned strainer and flow meter | Daimon A. Boccamazzo | Not Adjusted |  | 54 | 2017-11-06 11:55 | Daimon A. Boccamazzo
19 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 08:45 | 736 |  |  | 287 | [8 empty] | 0.2 | [13 empty] | ​everything good, cleaned strainer | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2017-09-13 08:48 | Daimon A. Boccamazzo
20 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:26 | 689 |  |  | 266 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-02 10:27 | RICHARD A. JOHNSON
21 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:17 | 684 |  | 9.16 | 212 | [8 empty] | 0.2 | [13 empty] | ​ | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-06-19 07:19 | RICHARD A. JOHNSON
22 | 1108 | 1108-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-04 12:16 | 760.6 | 94.3 | [10 empty] | 0.08 |  |  |  | 237900 | 314500 |  |  |  | Correct | Good | Dirty | Clean | Level Okay | ​​Not a free Chlorine feed day. Expected low Chlorine concentrations. Cleaned out strainer on controller. | reedhea |  |  |  | 2017-05-04 13:53 | reedhea
23 | 1108 | 1108-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-03-17 11:38 | 601 | 143 | 7.8 | [9 empty] | 0.99 |  |  |  | 2338200 | 311400 | 10 |  |  | Correct | Good | Dirty | Clean | Level Okay | ​​Cleaned strainer, recalibrated conductivity | reedhea |  |  |  | 2017-03-17 11:44 | reedhea
24 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-23 07:25 | [26 empty] | ​tower is offline for the winter | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-26 07:27 | Daimon A. Boccamazzo
25 | 1108 | 1108-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-12-13 13:38 | [16 empty] | 2323600 | 310100 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | reedhea |  |  |  | 2016-12-13 13:51 | reedhea
26 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-06 10:07 | 1060 |  | 8.1 | 100 | [8 empty] | 0 | [13 empty] | ​only a little bit of free chlorine in the tower because the tower is not running as much because it is cold outside so there is no demand for it. So it has no flow which makes the st70 pump miss the fed. | Daimon A. Boccamazzo | Not Adjusted |  | 59 | 2016-12-12 10:14 | Daimon A. Boccamazzo
27 | 1108 | 1108-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 11:11 | 710 | 134 | 7.7 | [9 empty] | 0.03 |  |  |  | 2323600 | 310000 |  |  |  | Correct | Good | Clean | Dirty | Level Okay | ​Sampled 30mins before ST70 biocide feed so free chlorine was expected to be low. Cleaned strainer. No flow. Water meters in gallons. | reedhea |  |  |  | 2016-11-09 11:38 | reedhea
28 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-19 14:06 | 578 |  | 8.9 | 173 | [8 empty] | 0.2 | [13 empty] | ​low free chlorine cause there was no, causing the feed to miss. Tower runs when needed so early in the mornings it won't run cause it's cold out side which means no flow to the controller | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-10-24 14:11 | Daimon A. Boccamazzo
29 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-19 10:19 | 579 |  | 8 | 149 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer. Controller still not working | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-07-20 10:21 | Daimon A. Boccamazzo
30 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:25 | 2029 |  | 8.2 | -75 | [8 empty] | 0.7 | [13 empty] | ​need to get chemicals hooked up asap! Had Rex call Matt from Nalco to manually turn on the bleed valve so the tower would drain some of the bad water out and get some fresh clean water in. | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-06-02 13:29 | Daimon A. Boccamazzo
31 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-18 12:24 | 1963 |  | 8.2 | 230 | [8 empty] | 0.14 | [13 empty] | ​all the chemicals are there and the new Nalco controller is mounted but needs to be set up and hooked up to the chemicals. Strainer will need to be cleaned next time around, need bucket up here. | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-05-18 12:27 | Daimon A. Boccamazzo
32 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-19 09:17 | 634 | 8 | 8.1 | 21167.7 | [8 empty] | 0 | [13 empty] | ​CH20 system Primed bromine pump | mrh4 | Not Adjusted |  |  | 2015-10-26 09:26 | mrh4
33 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-14 11:48 | 611 | 8 | 8.1 | 211 | [8 empty] | 0 | [13 empty] | ​CH20 system All test results are within parameters | mrh4 | Not Adjusted |  |  | 2015-10-16 11:52 | mrh4
34 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-14 13:36 | 577 |  | 8 | [23 empty] | TEI - 3 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 26.1 | 2015-09-21 13:36 | Jay Dahlstrom
35 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-10 13:02 | 571 |  | 8.1 | [23 empty] | TEI - 0 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 26.2 | 2015-09-21 13:02 | Jay Dahlstrom
36 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-03 12:58 | 581 |  | 8.1 | [23 empty] | TEI - 1 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 28.4 | 2015-09-21 12:58 | Jay Dahlstrom
37 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-19 12:46 | 530 |  | 8.6 | [23 empty] | ​TEI - 3 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 28.3 | 2015-09-21 12:47 | Jay Dahlstrom
38 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-23 09:23 | 551 |  | 8.1 | [23 empty] | ​TEI - 0 ppm POSCA - 8 ppm​ | mrh4 | Up |  | 25.2 | 2015-09-21 09:24 | Jay Dahlstrom
39 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-11 09:12 | 551 |  | 8.1 | [23 empty] | ​TEI - 0 ppm POSCA - 6 ppm | mrh4 | Not Adjusted |  | 23.7 | 2015-09-21 09:13 | Jay Dahlstrom
40 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-14 10:21 | 881 |  |  | 121 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 86 | 2018-10-01 10:22 | RICHARD A. JOHNSON
41 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-24 09:23 | 876.3 |  |  | 123 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 86 | 2018-07-30 09:24 | RICHARD A. JOHNSON
42 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-29 10:34 | 871.2 |  |  | 160 | [8 empty] | 0.5 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 87 | 2018-05-31 10:35 | RICHARD A. JOHNSON
43 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-22 07:48 | 879 |  |  | 148 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 85 | 2018-04-02 07:49 | RICHARD A. JOHNSON
44 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 10:22 | 875 |  |  | 219 | [8 empty] | 0.2 | [13 empty] | ​fed st70 for 30 mins to bring the FC levels up | Daimon A. Boccamazzo | Not Adjusted |  | 85 | 2018-03-16 10:29 | Daimon A. Boccamazzo
45 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-31 13:25 | 866 |  |  | 217 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 83 | 2018-02-01 13:25 | RICHARD A. JOHNSON
46 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-22 12:15 | 718 |  |  | 182 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 88 | 2017-12-04 12:16 | RICHARD A. JOHNSON
47 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 11:17 | 695 |  |  | 301 | [8 empty] | 0.2 | [13 empty] | ​​Changed st70 jug | Daimon A. Boccamazzo | Not Adjusted |  | 87 | 2017-09-11 11:31 | Daimon A. Boccamazzo
48 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:24 | 430 |  |  | 234 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 89 | 2017-08-02 10:25 | RICHARD A. JOHNSON
49 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:23 | 686 |  | 8.88 | 208 | [8 empty] | 2.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 86 | 2017-06-19 07:25 | RICHARD A. JOHNSON
50 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-04 12:15 | 738.4 | 101 | 8 |  | 90 | [6 empty] | 7 | 0.04 | 0.2 | 0.5 |  | 14.472 | 15223 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​System looks great - no adjustments needed. ​Dropped off the sump pump for transferring ST70 from the portafeed tank to the empty pails. | reedhea |  |  |  | 2017-05-04 13:24 | reedhea
51 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-04-07 10:44 | 816 | 123 | [10 empty] | 0.06 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​​ST70 leaking, free chlorine low. Replacement parts in stock now, working with Daimon to repair | reedhea |  |  |  | 2017-04-07 10:54 | reedhea
52 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-03-17 10:15 | 773 | 117 | 8.6 | [9 empty] | 0.06 |  |  |  | 1420.4 | 14134.4 | 11.9 | 0.4 | 0.02 | Not Correct | Good | Clean | Clean | Level Okay | ​​Date/time changed on trasar. ST70 pump airlocked; pump rerpimed and manually fed for 30 mins. | reedhea |  |  |  | 2017-03-17 10:28 | reedhea
53 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-02-08 14:20 | 725 | 122 | 8.4 | [9 empty] | 0.5 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​​ST70 portafeed leaking into containment basin - Nalco will follwo up | reedhea |  |  |  | 2017-02-08 15:56 | reedhea
54 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-23 07:22 | 742 |  | 8.9 | 240 | [8 empty] | 0.7 | [13 empty] | ​everything is okay. Tower is still running and it is supposed to be shut down during the winter | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2017-01-26 07:25 | Daimon A. Boccamazzo
55 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-12-13 13:33 | 720 | 148 | 8.4 | [9 empty] | 0.1 |  |  |  | 1366.8 | 12176 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Not an ST70 fed day Parameters were within spec. | reedhea |  |  |  | 2016-12-13 13:37 | reedhea
56 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-06 07:55 | 740 |  | 8.9 | 147 | [8 empty] | 1 | [13 empty] | ​everything is all good | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2016-12-07 07:57 | Daimon A. Boccamazzo
57 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 10:51 | 744 | 127 | 7.9 | [9 empty] | 0.1 |  |  |  |  | 1403 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Free chloirne low as it was not a feed day. | reedhea |  |  |  | 2016-11-09 11:07 | reedhea
58 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-19 14:03 | 750 |  | 9 | 163 | [8 empty] | 0.2 | [13 empty] | ​temp was pretty high. Free Chlorine was going to feed later on that day | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2016-10-24 14:06 | Daimon A. Boccamazzo
59 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-18 12:19 | 746 |  | 8.7 | 148 | [8 empty] | 0.3 | [13 empty] | ​strainer was clean, tower good, no leaks and no alarms | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2016-07-19 12:24 | Daimon A. Boccamazzo
60 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:22 | 734 |  | 8.8 | 177 | [8 empty] | 0.2 | [13 empty] | ​chemicals look good. Probably should order some st70 soon. No leaks on chemical system and the tower looks good no leaks or problems. | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2016-06-02 13:25 | Daimon A. Boccamazzo
61 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-16 22:49 | 725 | 206 | 8.7 |  | 270 | 274 |  | 0.58 | 4.7 | 7.1 | 0.35 | 0.1 | 0.03 | 0.124 | 0.52 |  | 1228.78 | 6937 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 22:53 | jrojas92
62 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-16 13:18 | 741 |  | 8.8 | 392 | [8 empty] | 0.15 | [13 empty] | ​relay 4 pumps every 3rd day at 3pm for 30mins. Relay 5 pumps every 3rd Friday at 10am for 30mins. I'm sure this is the reasoning for the free chlorine level being so low. Need to get the relays named or labeled on the pumps so we know what is what. The strainer is still good. | Daimon A. Boccamazzo | Not Adjusted |  | 85 | 2016-05-16 13:23 | Daimon A. Boccamazzo
63 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 14:27 | [12 empty] | 6.4 | [13 empty] | ​tested the free chlorine level at 2:00pm 5/4/16 and they were 6.4ppm which is above protocol and it stayed in the range for 24 hours. I also turned the blowdown valve back to auto | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 14:30 | Daimon A. Boccamazzo
64 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 09:12 | [12 empty] | 6.8 | [13 empty] | ​need the free chlorine levels to be above 5ppm until 1:50 pm 5/4/16. Pumped st70 into the system for 30 minutes to make sure we stay above 5ppm until testing it at 1:50 pm 5/4/16 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 09:15 | Daimon A. Boccamazzo
65 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-03 13:55 | [12 empty] | 5.3 | [13 empty] | ​pumped st70 into the system for another hour at 1:55pm | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-03 13:56 | Daimon A. Boccamazzo
66 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-03 13:13 | [12 empty] | 4.4 | [13 empty] | ​​4.4 ppm free chlorine at 10:35 am 03MAY16 | dn3 | Not Adjusted |  |  | 2016-05-03 13:16 | dn3
67 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-20 11:49 | [26 empty] | ​fixed connecting tube from porta feed to the pump, for the st70 chemical. Also ran the pump on manual for 5 minutes and there were no leaks | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-20 11:52 | Daimon A. Boccamazzo
68 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-20 08:57 | 746 |  | 7.5 | 260 | [8 empty] | 0.1 | [13 empty] | ​st70 is still offline due to porta feed issues | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-20 08:59 | Daimon A. Boccamazzo
69 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-18 20:44 | 1086 | 153 | 8.7 |  | 420 | 400 |  | 0.42 | 5.4 | 8.1 | 0.31 | 0 | 0.06 | 0.143 | 0.52 |  | 1116.89 | 5958 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Controller was turned off. | jrojas92 |  |  |  | 2016-06-06 20:57 | jrojas92
70 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-28 06:46 | 718 | 162 | 8.5 | 217 | [8 empty] | 0.5 | [14 empty] | Bob A Adams | Not Adjusted |  | 83.5 | 2016-03-29 06:48 | Bob A Adams
71 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-25 21:59 | 730 | 187 | 8.7 |  | 260 | 282 |  | 0.14 | 6 | 9.5 | 0.44 | 0 | 0.11 | 0.134 | 0.47 |  | 1103.49 | 5824 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​​White crust on bottom of ST70 PortaFeed tank basin. | jrojas92 |  |  |  | 2016-04-27 22:10 | jrojas92
72 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 14:09 | 731 | 148 | 8.6 | 210 | [8 empty] | 0.5 | [14 empty] | Bob A Adams | Not Adjusted |  | 87.8 | 2016-03-10 14:11 | Bob A Adams
73 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 11:23 | 739 | 95.7 | 8.4 | 272 | [8 empty] | 0.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 83.6 | 2016-02-08 11:24 | Bob A Adams
74 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-26 14:10 | 746 | 153 | 8.5 | 217 | [8 empty] | 0.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 86 | 2016-01-28 14:11 | Bob A Adams
75 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-12 14:25 | 947 | 152.2 | 8.6 | 153 | [8 empty] | 0.1 | [13 empty] | ​calibrated conductivity | Bob A Adams | Not Adjusted |  | 86 | 2016-01-12 14:27 | Bob A Adams
76 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 14:35 | 558 | 157 | 8.6 | 178 | [8 empty] | 0.4 | [13 empty] | ​chess good. Cond. calibrated | Bob A Adams | Not Adjusted |  | 86 | 2015-12-31 14:41 | Bob A Adams
77 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 13:54 | 725 | 199 | 8.6 |  | 290 | 290 |  | 0 | 5.4 | 10.2 | 0.38 | 0 | 0.03 | 0.1262 | 0.5 |  | 1029.12 | 3200 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-12-21 13:59 | jrojas92
78 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-10 11:38 | 748 | 142 | 8.68 | 0 | [8 empty] | 0 | [13 empty] | ​Slug fed biocide | mrh4 | Not Adjusted |  | 87.9 | 2015-11-24 11:42 | mrh4
79 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-04 14:53 | 747 | 130.1 | 8.7 | 148 | [8 empty] | 1 | [13 empty] | ​ | mrh4 | Not Adjusted |  | 83.7 | 2015-11-04 14:55 | mrh4
80 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-04 09:18 | 747 | 130.1 | 8.7 | [9 empty] | 1 | [14 empty] | mrh4 | Not Adjusted |  | 83.7 | 2015-11-23 09:21 | mrh4
81 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-23 14:26 | 747 | 198 | 8.7 |  | 270 | 304 |  | 0.17 | 4.5 | 10.5 | 0.48 | 0.1 | 0.04 | 0.179 | 0.54 |  | 1005 | 2376 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 14:32 | jrojas92
82 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-28 17:08 | 727 | 193 | 8.6 |  | 260 | 288 |  | 0 | 5.1 | 12.3 | 0.62 | 0.2 | 0.06 | 0.319 | 0.92 |  | 991.6 | 1780 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​First BD meter reading taken because of newly installed meter faceplate. | jrojas92 |  |  |  | 2015-09-30 17:34 | jrojas92
83 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-23 14:01 | 755 | 130.1 | 9 | [9 empty] | 0.5 | [14 empty] | mrh4 | Not Adjusted |  | 85.5 | 2015-09-23 14:04 | mrh4
84 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-24 16:13 | 727 | 187 | 8.6 |  | 270 | 300 |  | 1.42 | 4.48 | 7 | 0.34 | 0.7 | 0.05 | 0.126 | 0.71 |  | 964.8 |  |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 16:22 | jrojas92
85 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-07-17 11:49 | 755 | 199 | 8.5 |  | 270 | 298 |  | 0.49 | 5.5 | 9.6 | 0.53 | 0.8 | 0.05 | 0.23 | 1.46 |  | 949 | [5 empty] | Good | Clean | Clean | Level Okay | ​Calibrated conductivity meter | jrojas92 |  |  |  | 2015-08-18 12:10 | jrojas92
86 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-19 17:07 | 168 | 402 | 7.5 |  | 50 | 78 |  | 0.4 | 14.5 | 11.9 | 0.14 | 1.9 | 0.21 | 0.311 | 0.41 |  | 924.6 |  |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 17:12 | jrojas92
87 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-14 18:00 | 793 | 180 | 8.4 |  | 310 | 280 |  | 0.23 | 3.4 | 4.8 | 0.79 | 0 | 0 | 0.372 | 3.4 |  | 911.2 | [8 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:02 | jrojas92
88 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-04-24 18:40 | 864 | 230 | 8.6 |  | 260 | 340 |  | 0.38 | 5 | 3.8 | 0.62 | 0 | 0 | 0.335 | 4.9 |  | 884.4 | [8 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:43 | jrojas92
89 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-14 13:35 | 732 | 140.2 | 8.7 | [9 empty] | 0.75 | [13 empty] | Fahrenheit​ | mrh4 | Not Adjusted |  | 88.4 | 2015-09-21 13:36 | Jay Dahlstrom
90 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-01 12:51 | 511 | 122.1 | 8.6 | [9 empty] | 0.74 | [13 empty] | ​Fahrenheit​ | mrh4 | Not Adjusted |  | 88.1 | 2015-09-21 12:52 | Jay Dahlstrom
91 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-27 10:16 | 1099 |  |  | 213 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 59 | 2018-10-01 10:16 | RICHARD A. JOHNSON
92 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-22 11:42 | 927.1 |  |  | 113 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2018-08-30 11:43 | RICHARD A. JOHNSON
93 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 11:05 | 314 | [11 empty] | 0.3 |  |  | 174 | [10 empty] | ​tower is leaking from a water meter valve on the make up water line. A work order has been put in to get the leak fixed. | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2018-08-10 11:07 | Daimon A. Boccamazzo
94 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-12 09:18 | [27 empty] | Jay Dahlstrom | Not Adjusted |  |  | 2018-07-11 09:19 | Jay Dahlstrom
95 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-28 13:15 | 200.1 |  |  | 157 | [8 empty] | 0 | [13 empty] | ​ | RICHARD A. JOHNSON | Not Adjusted |  | 57 | 2018-06-29 13:17 | RICHARD A. JOHNSON
96 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:11 | 628 |  |  | 226 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-02 10:13 | RICHARD A. JOHNSON
97 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-17 13:26 | [26 empty] | ​couldn't get any water to test tower. System is in winter mode | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-17 13:27 | Daimon A. Boccamazzo
98 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-29 11:51 | 801 |  | 8.9 | 182 | [8 empty] | 0.3 | [13 empty] | ​cleaned strainer. Tower doesn't run too often because there isn't a big demand for it during the winter. | Daimon A. Boccamazzo | Not Adjusted |  | 59 | 2016-11-29 11:55 | Daimon A. Boccamazzo
99 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-06 14:45 | 566 |  | 8.9 | 147 | [8 empty] | 0 | [13 empty] | ​need 5 gallon bucket up there so I can clean the strainer and sensors without getting water everywhere. Also need a 5 gallon bucket of 3dt222 up there | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-09-06 14:48 | Daimon A. Boccamazzo
100 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-02 09:05 | 559 |  | 8.9 | 142 | [8 empty] | 0 | [13 empty] | ​both of the old chemical pumps are leaking. Strainer is good. Feeds keep missing and 3dt222 bucket is empty so need to get some up there | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-08-04 09:08 | Daimon A. Boccamazzo
101 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-30 08:38 | 563 |  | 8.9 | 154 | [8 empty] | 0.1 | [13 empty] | ​chemicals still not hooked up, strainer is cleaned. | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-07-08 08:40 | Daimon A. Boccamazzo
102 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-31 13:04 | 613 |  | 8.2 | 221 | [8 empty] | 0.2 | [13 empty] | ​need to get chemicals hooked up so system can start regular feelings of each chemical when needed. Didn't need to clean the strainer. Changed st70 feed to Monday-Friday at 12 pm for 30 minutes | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-05-31 13:07 | Daimon A. Boccamazzo
103 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 10:36 | 1020 |  | 8.9 | 204 | [8 empty] | 0.01 | [13 empty] | ​old walchem controller, cooling tower controller says "temp err". Orp and ph controller says normal. Still good amount of chemical in both buckets. Need to get a empty bucket up here | Daimon A. Boccamazzo | Not Adjusted |  | 80 | 2016-05-12 10:39 | Daimon A. Boccamazzo
104 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-25 14:11 | [26 empty] | ​tower not running. No load. Ready to run | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-25 14:11 | Daimon A. Boccamazzo
105 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-06 11:53 | 518 | 6 | 8.5 | 284 | [8 empty] | 2 | [13 empty] | ​posca in range. Calibrated temp | Bob A Adams | Not Adjusted |  | 76 | 2016-04-06 11:55 | Bob A Adams
106 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 08:27 | 597 | 8 | 8.5 | 289 | [8 empty] | 0.2 | [13 empty] | ​posca in range. Orp sensor needs to be replaced | Bob A Adams | Not Adjusted |  | 79 | 2016-03-25 08:29 | Bob A Adams
107 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 10:31 | 574 | 6 | 8.4 | 273 | [8 empty] | 0.5 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 72 | 2016-03-10 10:33 | Bob A Adams
108 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 14:05 | 597 | 6 | 7.5 | 305 | [8 empty] | 2 | [14 empty] | Bob A Adams | Not Adjusted |  | 75.5 | 2016-02-08 14:06 | Bob A Adams
109 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-25 13:46 | 652 | 8 | 8.5 | 154 | [8 empty] | 0.2 | [13 empty] | ​Posca in range. Cleaned sensors. | Bob A Adams | Not Adjusted |  | 75 | 2016-01-25 13:47 | Bob A Adams
110 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-06 13:50 | 615 | 8 | 8.5 | 165 | [8 empty] | 0.2 | [13 empty] | ​Posca and free chlorine in range. Cleaned sensors. Calibrated Temp | Bob A Adams | Not Adjusted |  | 76 | 2016-01-06 13:53 | Bob A Adams
111 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 07:21 | 576 | 6 | 8.6 | 390 | [8 empty] | 3.4 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 77 | 2015-12-31 07:24 | Bob A Adams
112 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:57 | 581 | 6 | 8.6 | 299 | [8 empty] | 1.2 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 78 | 2015-12-31 07:59 | Bob A Adams
113 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-01 06:52 | 635 | 8 | 8.6 | 276 | [8 empty] | 0.6 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 73 | 2015-12-04 06:54 | Bob A Adams
114 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-23 14:09 | 599 | 4 | 8.6 | 241 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 74 | 2015-11-30 14:13 | Bob A Adams
115 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-19 06:58 | 602 | 6 | 8.5 | 235 | [8 empty] | 0.6 | [13 empty] | ​cleaned sensors. Posca in range | Bob A Adams | Not Adjusted |  | 71 | 2015-11-20 07:01 | Bob A Adams
116 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-16 14:11 | 622 | 6 | 8.5 | 262 | [8 empty] | 0.6 | [13 empty] | ​Posca in range. Cleaned the sensors | Bob A Adams | Not Adjusted |  | 72 | 2015-11-16 14:13 | Bob A Adams
117 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-09 14:07 | 611 | 6 | 8.6 | 261 | [8 empty] | 0.5 | [13 empty] | ​​Posca in range. Cleaned the sensors | Bob A Adams | Not Adjusted |  | 73 | 2015-11-16 14:11 | Bob A Adams
118 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-05 14:23 | 571 | 6 | 8.4 | 222 | [8 empty] | 0.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 73 | 2015-10-05 14:26 | Bob A Adams
119 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-15 13:39 | 452 |  | 7.7 | [23 empty] | ​TEI - 3 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 11 | 2015-09-21 13:39 | Jay Dahlstrom
120 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-08-31 10:51 | [26 empty] | ​tower is now offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-09-11 10:53 | Daimon A. Boccamazzo
121 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-01-19 14:33 | 750 |  | 8.8 | 268 | [8 empty] | 0.3 | [13 empty] | ​tower will be removed soon | Daimon A. Boccamazzo | Not Adjusted |  | 79 | 2017-01-25 14:38 | Daimon A. Boccamazzo
122 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-12-01 13:29 | 1510 |  | 8.8 | 179 | [8 empty] | 0 | [13 empty] | ​still need to know how to work the controller | Daimon A. Boccamazzo | Not Adjusted |  | 77 | 2016-12-01 13:33 | Daimon A. Boccamazzo
123 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-10-14 13:27 | 662 |  | 8.9 | 166 | [8 empty] | 0.1 | [13 empty] | ​still the old system so I don't know how to use it so I can make adjustments | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-10-24 13:41 | Daimon A. Boccamazzo
124 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-09-08 13:14 | 645 |  | 8.9 | 153 | [8 empty] | 0.1 | [13 empty] | ​still don't know how to work the old walchem controllers. Would like to pump st70 into the system to bring the free chlorine levels up, I always get low readings of st70 | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-09-08 13:16 | Daimon A. Boccamazzo
125 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-08-08 10:38 | 630 |  | 8.9 | 138 | [8 empty] | 0.2 | [13 empty] | ​would like to figure out how to adjust the st70 feeding so I can try and bring the free chlorine levels up a little bit more. | Daimon A. Boccamazzo | Not Adjusted |  | 77 | 2016-08-08 10:45 | Daimon A. Boccamazzo
126 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-07-18 10:26 | 704 |  | 8.9 | 121 | [8 empty] | 0 | [13 empty] | ​changed unibrom plus bucket. Need to know how to use the walchem controllers so I can get the free chlorine levels up | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-07-18 10:29 | Daimon A. Boccamazzo
127 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-06-01 14:57 | 698 |  | 8.9 | 160 | [8 empty] | 0.1 | [13 empty] | ​tower looks good old what hem controller so I can tell when it feeds st70 into the tower. Also found a bucket of the 7341 chemical | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2016-06-01 14:59 | Daimon A. Boccamazzo
128 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-05-16 10:03 | 740 |  | 8.9 | 185 | [8 empty] | 0.23 | [13 empty] | ​system is normal. Probably going to need new bucket of posca next time around. Started pumping posca in the tower after I had taken a sample. Orp/ph controller said output timeout. Still old walchem system | Daimon A. Boccamazzo | Not Adjusted |  | 78 | 2016-05-16 10:08 | Daimon A. Boccamazzo
129 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-04-29 13:13 | 402 |  | 8.7 | 375 | [8 empty] | 0.5 | [13 empty] | ​good flow, still have good amount of chemical in the buckets and there are also extra buckets. Controllers both say normal on them. Also while I let the free chlorine test sit there the water turned more pink and I pressed the green button again to check the level and it read 1.4 | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-04-29 13:17 | Daimon A. Boccamazzo
130 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-04-07 14:28 | 476 | 4 | 8.4 | 292 | [8 empty] | 0.4 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 84 | 2016-04-07 14:29 | Bob A Adams
131 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-03-25 11:30 | 660 | 6 | 8.8 | 390 | [8 empty] | 1.7 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 76 | 2016-03-28 11:32 | Bob A Adams
132 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-03-16 11:17 | 628 | 6 | 8.5 | 334 | [8 empty] | 1.3 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 74.8 | 2016-03-16 11:19 | Bob A Adams
133 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-03-11 10:30 | 654 | 5 | 8.6 | 391 | [8 empty] | 1.9 | [13 empty] | ​​posca in range. Replaced bucket of posca | Bob A Adams | Not Adjusted |  | 75.5 | 2016-03-11 10:32 | Bob A Adams
134 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-02-22 14:00 | 643 | 4 | 8.4 | 257 | [8 empty] | 0.8 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 84 | 2016-02-22 14:01 | Bob A Adams
135 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 08:42 | 643 | 5 | 8.5 | 130 | [8 empty] | 0 | [13 empty] | ​Posca in range. Orp and conductivity were out of calibration. | Bob A Adams | Not Adjusted |  | 83.3 | 2016-02-08 08:49 | Bob A Adams
136 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-28 14:23 | 601 | 6 | 8.5 | 292 | [8 empty] | 1.2 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 81 | 2016-01-28 14:24 | Bob A Adams
137 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-15 09:00 | 560 | 6 | 8.5 | 357 | [8 empty] | 2.6 | [13 empty] | ​cleaned orp sensor. Clog in bromine line. Flow meter dirty causing flow meter to stick open. | Bob A Adams | Not Adjusted |  | 84 | 2016-01-15 09:04 | Bob A Adams
138 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 13:06 | 575 | 10 | 8.7 | 180 | [8 empty] | 0.1 | [13 empty] | ​calibrated conductivity & Orp | Bob A Adams | Not Adjusted |  | 75 | 2015-12-31 13:09 | Bob A Adams
139 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-12-08 10:00 | 327 | 8 | 8.1 | 269 | [8 empty] | 0 | [13 empty] | ​CH20 treatment system Primed bromine pump | mrh4 | Not Adjusted |  | 68 | 2015-12-14 10:02 | mrh4
140 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-11-10 11:35 | 634 | 8 | 8.1 | 231 | [8 empty] | 0 | [13 empty] | ​Primed bromine pump CH20 treatment system | mrh4 | Not Adjusted |  | 71.3 | 2015-11-24 11:37 | mrh4
141 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-11-04 14:51 | 571 | 8 | 8.1 | 223 | [8 empty] | 0 | [13 empty] | ​CH20 system Primed bromine pump | mrh4 | Not Adjusted |  | 74.1 | 2015-11-04 14:53 | mrh4
142 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-11-04 09:07 | 571 | 8 | 8.1 | 242 | [8 empty] | 0 | [13 empty] | ​CH20 treatment system Primed bromine pump | mrh4 | Not Adjusted |  | 74.1 | 2015-11-23 09:12 | mrh4
143 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-10-23 09:52 | 563 | 8 | 8.1 | 241 | [8 empty] | 6 | [13 empty] | ​CH20 system. Test results are in their parameters. Reduced ORP set point from 210 to 200 | mrh4 | Not Adjusted |  | 76.1 | 2015-10-26 09:57 | mrh4
144 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-10-15 11:54 | 562 | 8 | 8.1 | 301 | [8 empty] | 0 | [13 empty] | ​Primed bromine pump CH20 system | mrh4 | Not Adjusted |  | 76.1 | 2015-10-16 11:59 | mrh4
145 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-09-23 14:11 | 611 | 8 | 8.1 | [9 empty] | 0 | [13 empty] | ​​ | mrh4 | Up |  |  | 2015-09-23 14:14 | mrh4
146 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-23 14:04 | 611 | 8 | 8.1 | [9 empty] | 0 | [13 empty] | ​​CH2O system Increased bromine pump speed | mrh4 | Not Adjusted |  |  | 2015-09-23 14:11 | mrh4
147 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-17 11:34 | [27 empty] | Bob A Adams | Not Adjusted |  |  | 2015-09-17 11:44 | dn3
148 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-13 13:34 | 581 |  | 8.1 | [23 empty] | ​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 21.6 | 2015-09-21 13:35 | Jay Dahlstrom
149 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-06 13:01 | 588 |  | 8.2 | [23 empty] | TEI - 0 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 22.7 | 2015-09-21 13:02 | Jay Dahlstrom
150 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-01 12:54 | 631 |  | 8.1 | [23 empty] | TEI - 0 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 23.4 | 2015-09-21 12:55 | Jay Dahlstrom
151 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-12 10:42 | 581 |  | 8.5 | [23 empty] | ​​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 23.3 | 2015-09-21 10:42 | Jay Dahlstrom
152 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-03 10:21 | 607 |  | 8.2 | [23 empty] | ​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 21.1 | 2015-09-21 10:22 | Jay Dahlstrom
153 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-25 10:11 | 564 |  | 8.2 | [23 empty] | ​​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 23.7 | 2015-09-21 10:12 | Jay Dahlstrom
154 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-20 09:20 | 606 |  | 8 | [23 empty] | ​TEI - 6 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 25.3 | 2015-09-21 09:20 | Jay Dahlstrom
155 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-20 09:00 | 597 |  | 8.3 | [23 empty] | ​TEI - 0 ppm POSCA - 8 ppm Primed Bromine pump and running flush | mrh4 | Not Adjusted |  | 26.2 | 2015-09-21 09:01 | Jay Dahlstrom
156 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-15 08:58 | 609 |  | 8.3 | [24 empty] | mrh4 | Not Adjusted |  | 24.4 | 2015-09-21 08:59 | Jay Dahlstrom
157 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:31 | 781.9 |  |  | 157 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 80 | 2018-08-30 11:32 | RICHARD A. JOHNSON
158 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 11:15 | 795 |  |  | 190 | [8 empty] | 0.3 | [13 empty] | ​two of the chemical pumps are air locked so they need to be changed out. | Daimon A. Boccamazzo | Not Adjusted |  | 83 | 2018-08-10 11:18 | Daimon A. Boccamazzo
159 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-28 13:08 | 271 |  |  | 173 | [8 empty] | 0.4 | [13 empty] | ​ | RICHARD A. JOHNSON | Not Adjusted |  | 77 | 2018-06-29 13:10 | RICHARD A. JOHNSON
160 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-25 13:27 | 797.6 |  |  | 151 | [8 empty] | 2.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 75 | 2018-04-30 13:28 | RICHARD A. JOHNSON
161 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-20 10:18 | 1077 |  |  | 142 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2018-02-23 10:19 | RICHARD A. JOHNSON
162 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-27 13:50 | 610 |  |  | 226 | [8 empty] | 1.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 77 | 2017-12-29 13:51 | RICHARD A. JOHNSON
163 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-19 10:29 | 102.5 |  |  | 180 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 75 | 2017-10-23 10:31 | RICHARD A. JOHNSON
164 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:11 | 343 |  |  | 196 | [8 empty] | 1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 79 | 2017-08-24 08:13 | RICHARD A. JOHNSON
165 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 07:41 | 290 |  |  | 157 | [8 empty] | 1.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 79 | 2017-08-02 07:42 | RICHARD A. JOHNSON
166 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-18 13:16 | 105 |  | 9 | 222 | [8 empty] | 0 | [13 empty] | ​started feeding st70 when I was leaving. Tower is constantly draining water cause tower one is constantly running make up water. | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2017-01-25 13:21 | Daimon A. Boccamazzo
167 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-01 13:18 | 80 |  | 9.2 | 184 | [8 empty] | 0.6 | [14 empty] | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-12-01 13:21 | Daimon A. Boccamazzo
168 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-07 10:17 | 223 |  | 9.5 | 175 | [8 empty] | 0.3 | [13 empty] | ​conductivity sensor needs to be calibrated | Daimon A. Boccamazzo | Not Adjusted |  | 77 | 2016-10-14 10:22 | Daimon A. Boccamazzo
169 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-07 07:08 | 203 |  | 8.8 | 152 | [8 empty] | 0.1 | [13 empty] | ​strainer good, conductivity and flow sensors good as well. Conductivity way too low but there are no alarms for it | Daimon A. Boccamazzo | Not Adjusted |  | 81 | 2016-09-08 07:11 | Daimon A. Boccamazzo
170 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-04 10:20 | 432 |  | 8.7 | 167 | [8 empty] | 1.7 | [13 empty] | ​strainer good. Just need to calibrate conductivity sensor cause it is reading 665 and I got 432 | Daimon A. Boccamazzo | Not Adjusted |  | 81 | 2016-08-08 10:23 | Daimon A. Boccamazzo
171 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-28 13:41 | 438 |  | 8.8 | 180 | [8 empty] | 1.5 | [13 empty] | ​need to check calibration on conductivity sensor, it is reading 665 and my meter is reading 438. | Daimon A. Boccamazzo | Not Adjusted |  | 81 | 2016-07-29 13:45 | Daimon A. Boccamazzo
172 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-01 07:53 | 141 |  | 8.7 | 177 | [8 empty] | 0.1 | [13 empty] | ​need chemicals to be hooked up just waiting on Beth to get some time to do that. Strainer is fine. Conductivity sensor needs to be calibrated the controller is reading 410 and my meter is reading 141 | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2016-06-01 07:57 | Daimon A. Boccamazzo
173 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 13:15 | 173 |  | 8.6 | 307 | [8 empty] | 0.04 | [13 empty] | ​cleaned strainer out. Chemicals are here but not hooked up need to get them hooked up asap | Daimon A. Boccamazzo | Not Adjusted |  | 82 | 2016-05-12 13:17 | Daimon A. Boccamazzo
174 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 08:53 | 140 |  | 7.4 | 305 | [8 empty] | 0 | [13 empty] | ​chemicals are here but they are not hooked up yet. Chemical loop strainer is really dirty and needs to be cleaned but I didn't have a bucket to dump the water in. Also there was an alarm for low flow | Daimon A. Boccamazzo | Not Adjusted |  | 80 | 2016-04-29 08:57 | Daimon A. Boccamazzo
175 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-06 13:58 | 165 | 0 | 8.3 | 213 | [8 empty] | 0 | [13 empty] | ​slug fed posca and bromine into cooling tower | Bob A Adams | Not Adjusted |  | 80 | 2016-04-06 14:01 | Bob A Adams
176 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 13:53 | 276 | 0 | 7.8 | 246 | [8 empty] | 0 | [13 empty] | ​Waitng for pump and controller to be programmed | Bob A Adams | Not Adjusted |  | 78 | 2016-03-31 13:58 | Bob A Adams
177 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-05 14:12 | 74 | 0 | 8.6 | 328 | [8 empty] | 1 | [13 empty] | ​towers were not running | Bob A Adams | Not Adjusted |  | 48.4 | 2016-02-05 14:14 | Bob A Adams
178 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-15 14:02 | 170 | 0 | 8.2 | 405 | [8 empty] | 4.2 | [13 empty] | ​Added Bromine the day before. Added Posca just before testing. Pumps were not running | Bob A Adams | Not Adjusted |  | 74 | 2016-01-15 14:05 | Bob A Adams
179 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-24 14:04 | 421 | 8 | 9.28 | [9 empty] | 0.67 | [13 empty] | ​​CH20 controls remain offline until booster pump is installed. Currently manually feeding chemicals at proper levels | mrh4 | Not Adjusted |  | 68.8 | 2015-09-24 14:26 | mrh4
180 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 13:56 | 81 |  | 7.9 | [23 empty] | TEI - 0 ppm POSCA ---​ | mrh4 | Not Adjusted |  | 22.7 | 2015-09-21 13:57 | Jay Dahlstrom
181 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-17 09:18 | 174 |  | 8.1 | [23 empty] | ​​TEI - o ppm POSCA - 4 ppm | mrh4 | Not Adjusted |  | 11.4 | 2015-09-21 09:19 | Jay Dahlstrom
182 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-20 10:12 | 687.2 |  |  | 239 | [8 empty] | 6.7 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-10-01 10:13 | RICHARD A. JOHNSON
183 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:33 | 1035 |  |  | 147 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-08-30 11:34 | RICHARD A. JOHNSON
184 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 10:56 | 1348 |  |  | 193 | [8 empty] | 0.1 | [13 empty] | ​still need to get the leak on the top of the tower fixed. Cleaned the water that was on the floor. Tower will feed st70 tomorrow | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2018-08-10 10:59 | Daimon A. Boccamazzo
185 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 06:58 | 1345 |  |  | 248 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-07-03 06:58 | RICHARD A. JOHNSON
186 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-23 13:24 | 1257 |  |  | 261 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2018-04-30 13:25 | RICHARD A. JOHNSON
187 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-22 10:11 | 599.1 |  |  | 199 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-02-23 10:12 | RICHARD A. JOHNSON
188 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-27 13:56 | 788 |  |  | 302 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2017-12-29 13:57 | RICHARD A. JOHNSON
189 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:23 | 641 |  |  | 208 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2017-08-24 08:24 | RICHARD A. JOHNSON
190 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 07:37 | 589 |  |  | 131 | [8 empty] | 0 | [13 empty] | ​tested on an off day | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-02 07:38 | RICHARD A. JOHNSON
191 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-05 13:16 | 880 |  | 9 | 190 | [8 empty] | 8.8 | [13 empty] | ​tower just fed st70 which is why the free chlorine levels are so high | Daimon A. Boccamazzo | Not Adjusted |  | 64 | 2017-01-17 13:18 | Daimon A. Boccamazzo
192 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-29 11:37 | 1057 |  | 8.5 | 166 | [8 empty] | 0 | [13 empty] | ​adjusted st70 pump from 60 to 80 | Daimon A. Boccamazzo | Up | 80 | 71 | 2016-11-29 11:41 | Daimon A. Boccamazzo
193 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-06 09:13 | 1486 |  | 9.2 | 173 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer and conductivity sensor. Drained water to bring conductivity down and then fed st70. Chemical pumps keep missing their feeds. | Daimon A. Boccamazzo | Not Adjusted |  | 71 | 2016-10-14 09:17 | Daimon A. Boccamazzo
194 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-06 14:39 | 651 |  | 8.9 | 142 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Oxi bio and non oxi bio are still alarming for missed feeds | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-09-06 14:42 | Daimon A. Boccamazzo
195 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-01 11:04 | 556 |  | 8.8 | 127 | [8 empty] | 0.1 | [13 empty] | ​need to find out why the feed times keep missing. Cleaned strainer. Need to check calibration on conductivity sensor cause it is reading 1334 and my meter is reading 556 | Daimon A. Boccamazzo | Not Adjusted |  | 77 | 2016-08-02 11:33 | Daimon A. Boccamazzo
196 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-29 11:58 | [26 empty] | ​tower has no water in it due to plumbers replacing leaking spray pump. Also need to replace conductivity sensor with the right replacement | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-06-29 12:00 | Daimon A. Boccamazzo
197 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-27 11:52 | 2100 |  | 8.9 | 171 | [8 empty] | 0.3 | [13 empty] | ​feed missed for h550 and st70 cause they were both off . I turned them both on and I feed st70 into the system at 80 for 5 mins and set a weekly timer for Monday, Wednesday, and Friday for one hour at 8 o'clock am. Put all pumps at 60 percent and made sure all pumps were on. Found a steady drip leak coming from the spray pump | Daimon A. Boccamazzo | Up | 60 | 75 | 2016-05-27 11:58 | Daimon A. Boccamazzo
198 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-10 14:51 | 1242 |  | 8.9 | 237 | [8 empty] | 0.04 | [13 empty] | ​tower is on. Chemicals are there but the pumps are not plugged in. Cleaned out chemical loop strainer | Daimon A. Boccamazzo | Not Adjusted |  | 77 | 2016-05-10 14:53 | Daimon A. Boccamazzo
199 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-22 08:41 | 525 |  | 7.8 | 283 | [8 empty] | 0 | [13 empty] | ​chemicals are there and all full but the system is not plugged in and running yet. Also cleaned out the chemical loop filter | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-22 08:45 | Daimon A. Boccamazzo
200 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-04 12:51 | 714 | 0 | 8.4 | 175 | [8 empty] | 0 | [13 empty] | ​waiting on the the Nalco controller to be programmed and chemicals hooked up. | Bob A Adams | Not Adjusted |  | 76 | 2016-04-04 12:54 | Bob A Adams
201 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-28 06:41 | 492 | 0 | 8.6 | 209 | [8 empty] | 0 | [13 empty] | ​​waiting for chemical system to be started up. | Bob A Adams | Not Adjusted |  |  | 2016-03-29 06:46 | Bob A Adams
202 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-07 08:55 | 768 | 4 | 8.6 | 339 | [8 empty] | 0 | [14 empty] | Bob A Adams | Not Adjusted |  | 68.5 | 2016-03-07 08:56 | Bob A Adams
203 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-11 08:26 | 788 | 0 | 8.5 | 152 | [8 empty] | 0 | [13 empty] | ​put chemical in feeder | Bob A Adams | Not Adjusted |  | 70 | 2016-02-12 08:31 | Bob A Adams
204 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-06 13:46 | 816 | 2 | 8.7 | 194 | [8 empty] | 0.1 | [13 empty] | ​ | Bob A Adams | Not Adjusted |  | 73 | 2016-01-06 13:48 | Bob A Adams
205 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:48 | 810 | 2 | 8.7 | 300 | [8 empty] | 0.6 | [13 empty] | ​ | Bob A Adams | Not Adjusted |  | 71 | 2015-12-31 07:50 | Bob A Adams
206 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-11 07:18 | 804 | 2 | 8.6 | 226 | [8 empty] | 0 | [13 empty] | ​ | Bob A Adams | Not Adjusted |  | 74 | 2015-12-31 07:21 | Bob A Adams
207 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-11 07:05 | 515 | 4 | 8.4 | 244 | [8 empty] | 0 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 72 | 2015-12-31 07:10 | Bob A Adams
208 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-06 14:38 | 617 | 4 | 8.6 | 600 | [8 empty] | 8.8 | [14 empty] | Bob A Adams | Not Adjusted |  | 75.2 | 2015-11-06 14:39 | Bob A Adams
209 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-28 06:58 | 2864 | 0 | 8.8 | 260 | [8 empty] | 0 | [13 empty] | ​calibrated conductivity | Bob A Adams | Not Adjusted |  | 74.3 | 2015-11-03 07:01 | Bob A Adams
210 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-05 13:32 | 689 |  | 8.6 | [23 empty] | ​ORP - 300 TWO - .7 OP - 4 | mrh4 | Not Adjusted |  | 73.2 | 2015-09-22 13:33 | Jay Dahlstrom
211 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-28 13:31 | 755 |  | 8.6 | [23 empty] | ​​ORP - 675 TWO - Too High OP - 24 | mrh4 | Not Adjusted |  | 73 | 2015-09-22 13:31 | Jay Dahlstrom
212 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 13:30 | 702 |  | 8.7 | [23 empty] | ​ORP - 450 TWO - 1.1 OP - .2 | mrh4 | Not Adjusted |  | 72 | 2015-09-22 13:31 | Jay Dahlstrom
213 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-15 13:41 | 631 |  | 8 | [23 empty] | ​TEI - 20+ ppm POSCA - 20+ ppm | mrh4 | Not Adjusted |  | 24.3 | 2015-09-21 13:41 | Jay Dahlstrom
214 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-04 13:29 | 679 |  | 8.5 | [23 empty] | ​ORP - 610 TWO - 4.2 OP - Too high | mrh4 | Not Adjusted |  | 72 | 2015-09-22 13:30 | Jay Dahlstrom
215 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-05 13:23 | 751 |  | 8.6 | [23 empty] | ​ORP - 560 TWO - 4.5 OP - 24 | mrh4 | Not Adjusted |  | 70.1 | 2015-09-22 13:28 | Jay Dahlstrom
216 | 1153 | 1153-Ccondenser_Water-NALCO | Condenser Water | NALCO | 2015-09-29 18:51 | 449 | 166 | 8.3 |  | 120 | 102 |  | 0 | 4.1 | 7.9 | 2.3 | 0.8 | 0.01 | 0.1201 | 0.59 |  | 8339 | 5730 |  |  |  |  | Good | Clean |  | Needs Filling | ​Chemical tubing is broken and cracked from exposure to the sun/heat. ST70 bucket is nearly empty. | jrojas92 |  |  |  | 2015-09-30 18:58 | jrojas92
217 | 1153 | 1153-Ccondenser_Water-NALCO | Condenser Water | NALCO | 2015-07-16 13:36 | 2543 | 286 | 8 |  | 280 | 100 |  | 0.46 | 10.7 | 12.2 | 4.7 | 0.6 | 13.9 | 0.248 | 0.97 |  | 8056 | 5730 | [5 empty] | Clean |  | Needs Filling | ​​Cooling tower was not running, and there was no flow through the injection quill (flow switch). The controller had low conductivity alarm because there was no flow through the probe. Low on ST-70 inventory. | jrojas92 |  |  |  | 2015-08-18 13:49 | jrojas92
218 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-14 10:24 | 864 |  |  | 145 | [8 empty] | 8.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 59 | 2018-10-01 10:25 | RICHARD A. JOHNSON
219 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-26 09:27 | 608.1 |  |  | 182 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-07-30 09:27 | RICHARD A. JOHNSON
220 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 08:54 | 260 |  |  | 175 | [8 empty] | 0.6 | [13 empty] | ​fed st70 for 30mins at 100% tower is still on stand by. | Daimon A. Boccamazzo | Not Adjusted |  | 48 | 2018-03-16 09:08 | Daimon A. Boccamazzo
221 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 11:11 | [26 empty] | ​could not get a sample. Spray pump needs to be replaced | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-09-11 11:12 | Daimon A. Boccamazzo
222 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:07 | 1050 |  | 9.22 | 183 | [8 empty] | 7.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 60 | 2017-06-19 07:09 | RICHARD A. JOHNSON
223 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-04 12:51 | 258.9 | 111.75 | [10 empty] | 0 | [8 empty] | Correct | Good | Dirty |  | Needs Filling | ​​There was no flow through the system due to bio growth restricting flow. The system was cleaned of debri and flow restoredd. The conductivty was low due to continued overflow. The blowdown solenoid was verified to be working properly so the overflow is occuring due to the basin water level. Free chlorine was 0.0 ppm because the ST70 chemical pail is empty. I also found the H550 near empty and was able to switch it out with an extra that was on the rooftop. | reedhea |  |  |  | 2017-05-04 12:56 | reedhea
224 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-03-31 10:18 | 230 | 102 | 7.3 | [9 empty] | 0 |  |  |  | 3057.3 | 100.54 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Conductivity low. Drain still leaking. | reedhea |  |  |  | 2017-03-31 10:20 | reedhea
225 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-02-08 10:33 | 244 | 122 | 7.6 | [9 empty] | 0.2 |  |  |  | 26667 | 100.54 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​MU meter in Cuft. BD darin leaking. Possible overflow or leaking solenoid | reedhea |  |  |  | 2017-02-08 10:37 | reedhea
226 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-20 07:16 | 320 |  | 9.3 | 250 | [8 empty] | 0 | [13 empty] | ​scheduled to feed st70 at 4pm. Tower is still on hand until needed | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2017-01-26 07:19 | Daimon A. Boccamazzo
227 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-12-13 13:12 | 205 | 108 | 7.5 | [9 empty] | 0.11 |  |  |  | 1987 | 100.54 |  |  |  | Correct | Good | Clean | Clean | Needs Filling | ​​MU METER IN CU FT. ST70 PAIL EMPTY CONDUCTIVITY RECALIBRATED | reedhea |  |  |  | 2016-12-13 13:17 | reedhea
228 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-05 07:48 | 226 |  | 10.3 | 137 | [8 empty] | 0.3 | [13 empty] | ​tower still on stand by | Daimon A. Boccamazzo | Not Adjusted |  | 42 | 2016-12-07 07:51 | Daimon A. Boccamazzo
229 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 10:35 | 705 | 110 | 7.7 | [9 empty] | 0.53 |  |  |  | 1780 | 100.54 | 17 |  |  | Correct | Good | Clean | Clean | Level Okay | ​Make-up meter is in cu ft not gallons. Two point calibration completed on controller conductivity. | reedhea |  |  |  | 2016-11-09 10:38 | reedhea
230 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-18 13:48 | 600 |  | 9.4 | 200 | [8 empty] | 8.8 | [13 empty] | ​strainer goo but conductivity probe needs calibration. Also there was an alarm saying relay 7 timed out but not sure what relay 7 is for | Daimon A. Boccamazzo | Not Adjusted |  | 50 | 2016-10-24 13:52 | Daimon A. Boccamazzo
231 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-08 13:19 | 251 |  | 8.8 | 165 | [8 empty] | 0.1 | [13 empty] | ​plugged in controller, it just needs to be programmed now. Cleaned strainer. Also the pumps need to be hard wired in to the controller. I plugged in the st70 pump into another outlet and pumped some into the system at 100% for about tens minutes and brought the free chlorine levels up to 3.4 | Daimon A. Boccamazzo | Not Adjusted |  | 60 | 2016-09-08 13:24 | Daimon A. Boccamazzo
232 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-18 10:32 | 256 |  | 8.7 | 145 | [8 empty] | 0.1 | [13 empty] | ​need to figure out if the tower needs to be drained or not cause it is hardly used. New controller is there but not plugged in | Daimon A. Boccamazzo | Not Adjusted |  | 56 | 2016-07-18 10:35 | Daimon A. Boccamazzo
233 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:15 | 364 |  | 8.6 | 175 | [8 empty] | 0 | [13 empty] | ​tower is still off line until needed. Chemicals are full and there is an extra h-550 and st70 bucket up there as well. | Daimon A. Boccamazzo | Not Adjusted |  | 63 | 2016-06-02 13:18 | Daimon A. Boccamazzo
234 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-22 23:35 | 345 | 0 | 7.8 |  | 80 | 64 |  |  | 0 | 0 | 1.49 | 0 | 0 | 0.146 | 0.71 |  | 126 | 100 |  |  |  | Correct |  |  |  | Level Okay | Tower & controller were off. | jrojas92 |  |  |  | 2016-06-06 23:39 | jrojas92
235 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-18 12:20 | 397 |  | 8.5 | 285 | [8 empty] | 0.06 | [13 empty] | ​old walchem controller but new Nalco pumps. Tower is on but still not running. Controller for the chemical feed is not turned on | Daimon A. Boccamazzo | Not Adjusted |  | 56 | 2016-05-18 12:23 | Daimon A. Boccamazzo
236 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-29 22:08 | 352 | 0 | 8 |  | 60 | 52 |  | 0.12 | 0.3 | 0 | 1.26 | 0.1 | 1.02 | 0.135 | 0.67 |  | 113 | 100 |  |  |  | Correct |  |  |  | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 22:12 | jrojas92
237 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 07:24 | [26 empty] | cooling tower is off, all chemicals are full plus there are extra chemicals there as well. Also I changed the speed to 60 on both the st70 and the h-550 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-02 07:27 | Daimon A. Boccamazzo
238 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-08 14:10 | 361 | 250 | 8.5 | 400 | [8 empty] | 8.5 | [13 empty] | ​bled system for 10 minutes | Bob A Adams | Not Adjusted |  | 61 | 2016-04-08 14:12 | Bob A Adams
239 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-25 20:04 | 523 | 0 | 10.1 |  | 40 | 30 |  | 0 | 0.3 | 0 | 0.16 | 0.1 | 81 | 0.067 | 0.14 |  | 53 | 89 | [7 empty] | Level Okay | ​Tower was BD for ~10min because high free Cl. Tower & controller off. | jrojas92 |  |  |  | 2016-06-06 20:08 | jrojas92
240 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 06:28 | 610 | 250 | 10.1 | 500 | [8 empty] | 8.8 | [13 empty] | ​Chemical system continues to pump when cooling tower is not running. Drained water to lower chemical level. | Bob A Adams | Not Adjusted |  | 51 | 2016-03-29 06:34 | Bob A Adams
241 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-22 13:20 | 1633 | 200 | 10 | 303 | [8 empty] | 8.8 | [13 empty] | ​controller kept feeding chemical when tower was not running. Turned off controller until I can program not to pump with no flow. Drained half water and filled. | Bob A Adams | Not Adjusted | 49.7 |  | 2016-02-22 13:24 | Bob A Adams
242 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-12 14:26 | 4424 | 250 | 11.1 | 380 | [8 empty] | 3.5 | [13 empty] | ​Drained tower water and filled back up. Trasar was reading Hi Conc. | Bob A Adams | Not Adjusted |  | 54.6 | 2016-02-12 14:31 | Bob A Adams
243 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-05 14:19 | 2818 | 250 | 9.8 | 300 | [8 empty] | 9.8 | [13 empty] | ​Trasar reading said "Hi". Had to turn tower on hand to get water flowing | Bob A Adams | Not Adjusted |  | 49.7 | 2016-02-05 14:22 | Bob A Adams
244 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 13:47 | 289 | 6.2 | 8.4 |  | 120 | 122 |  | 0.26 | 0.6 | 0 | 0.39 | 0.4 | 0 | 0.0447 | 0.05 |  | 8800 | 5736 | [5 empty] | Clean |  |  | Needs more ST70 chemical (<1/2 gal). | jrojas92 |  |  |  | 2015-12-22 13:55 | jrojas92
245 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-29 15:12 | 416 | 118 | 8.3 |  | 120 | 116 |  | 0.82 | 3.3 | 5.5 | 1.87 | 0.7 | 0.01 | 0.114 | 0.41 |  | 8373 | 5736 | [7 empty] | Needs Filling | ​Needs more ST70 chemical. | jrojas92 |  |  |  | 2015-11-14 15:16 | jrojas92
246 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-26 16:49 | 1612 | 309 | 8.2 |  | 170 | 78 |  | 0 | 9.6 |  | 4.26 | 1.2 | 0 | 0.205 | 1.3 |  | 8115 | 5730 | [8 empty] | ​Chem tubing is cracked/broken | jrojas92 |  |  |  | 2015-11-14 16:52 | jrojas92
247 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-19 17:40 | 3642 | 322 | 8.9 |  | 320 | 98 |  | 0.06 | 11.9 | 10.9 | 5.56 | 1.1 | 0.16 | 0.225 | 0.56 |  | 7965 | 5720 | [9 empty] | jrojas92 |  |  |  | 2015-11-14 17:42 | jrojas92
248 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-28 18:30 | 2032 | 305 | 8 |  | 200 | 94 |  | 1.46 | 11.9 | 11.4 | 5.02 | 0.4 | 0.02 | 0.195 | 0.39 |  | 7905 | 5710 | [7 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:32 | jrojas92
249 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-20 08:54 | 577 |  | 7 | [9 empty] | 0.23 | [13 empty] | ​POSCA --- | mrh4 | Not Adjusted |  | 22.4 | 2015-09-22 08:55 | Jay Dahlstrom
250 | 1119 | 1119-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-06 11:55 | [26 empty] | ​tower is closed down. Water, power, chemicals turned off | Bob A Adams | Not Adjusted |  |  | 2016-04-06 11:56 | Bob A Adams
251 | 1119 | 1119-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 08:30 | 0 | 0 | 0 | 0 | [8 empty] | 0 | [13 empty] | ​Towers are drained and turned off of chemicals and power | Bob A Adams | Not Adjusted |  | 0 | 2016-03-25 08:31 | Bob A Adams
252 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-17 10:22 | 1570 |  |  | 143 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-10-01 10:23 | RICHARD A. JOHNSON
253 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-27 09:20 | 1006 |  |  | 185 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-07-30 09:21 | RICHARD A. JOHNSON
254 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-29 10:35 | 468.9 |  |  | 148 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2018-05-31 10:36 | RICHARD A. JOHNSON
255 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-26 07:56 | 159.8 |  |  | 169 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-04-02 07:57 | RICHARD A. JOHNSON
256 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-27 11:04 | 72 |  |  | 189 | [8 empty] | 0.1 | [13 empty] | ​tower is still making up water. Trying to get it fixed | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2018-03-16 11:23 | Daimon A. Boccamazzo
257 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-30 13:21 | 84 |  |  | 202 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-02-01 13:22 | RICHARD A. JOHNSON
258 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-21 12:08 | 124 |  |  | 161 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-12-04 12:10 | RICHARD A. JOHNSON
259 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-30 08:22 | 80 |  |  | 196 | [8 empty] | 0.8 | [13 empty] | ​manually closed make up water valve so it would stop over flowing the tower until I can fix the solenoid valve | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2017-11-06 08:36 | Daimon A. Boccamazzo
260 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 08:52 | 147 |  |  | 265 | [8 empty] | 0.2 | [13 empty] | ​st70 will feed tomorrow. FC reading good for an off day | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2017-09-13 08:58 | Daimon A. Boccamazzo
261 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:22 | 3096 |  | 8.61 | 183 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 61 | 2017-06-19 07:23 | RICHARD A. JOHNSON
262 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-10 13:27 | 2750 | 130 | 8.9 | [9 empty] | 0 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​​Chemistry looks good - conductivity is high. Troubleshooting blowdown solenoid. | reedhea |  |  |  | 2017-05-10 13:28 | reedhea
263 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-23 07:32 | 2236 |  | 8.7 | 266 | [8 empty] | 0.1 | [13 empty] | ​will feed st70 at 2pm for 1hr. Not too worried about the low FC levels cause it doesn't feed over the weekend. | Daimon A. Boccamazzo | Not Adjusted |  | 51 | 2017-01-26 07:35 | Daimon A. Boccamazzo
264 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-12-13 14:18 | 2542 | 111 | 8.4 | [9 empty] | 0.12 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​Conductivity is high - | reedhea |  |  |  | 2016-12-13 14:22 | reedhea
265 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-06 10:15 | 2580 |  | 8.7 | 150 | [8 empty] | 0.6 | [13 empty] | ​need to get the tower clean so the conductivity will go down | Daimon A. Boccamazzo | Not Adjusted |  | 63 | 2016-12-12 10:17 | Daimon A. Boccamazzo
266 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 13:05 | 2482 | 163 | 8.3 | [9 empty] | 0 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​System was in blowdown lock-out mode. I manually set the controller to blowdown for 30mins to decrease conductivity. | reedhea |  |  |  | 2016-11-09 13:29 | reedhea
267 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-20 14:17 | 2980 |  | 9 | 173 | [8 empty] | 0.3 | [13 empty] | ​can't get conductivity to go down, even when I drain water out of the system it barley moves the number down | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-10-24 14:25 | Daimon A. Boccamazzo
268 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-19 10:21 | 1613 |  | 8.7 | 139 | [8 empty] | 1.1 | [13 empty] | ​cleaned tower, changed side stream filter, and everything else is good | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2016-07-20 10:24 | Daimon A. Boccamazzo
269 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:30 | 641 |  | 8.8 | 115 | [8 empty] | 0.1 | [13 empty] | ​strainer is clean. Tower looks good, no problems or leaks | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-06-02 13:34 | Daimon A. Boccamazzo
270 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-16 23:00 | 708 | 183 | 8.6 |  | 250 | 286 |  | 0.69 | 4.4 | 4.7 | 0.14 | 0 | 0 | 0.125 | 0.14 |  | 1416570 | 170580 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 23:03 | jrojas92
271 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-16 13:13 | 725 |  | 8.77 | 243 | [8 empty] | 0.52 | [13 empty] | ​all systems good strainer didn't need to cleaned, no leaks or problems | Daimon A. Boccamazzo | Not Adjusted |  | 61 | 2016-05-18 13:15 | Daimon A. Boccamazzo
272 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-28 14:11 | 734 |  | 8 | 294 | [8 empty] | 0.1 | [13 empty] | ​changed copper corrosion sensor, loosened chemical loop filter. Also changed the trasar chemical pump and fixed the h550 leak and also primed both of those Chicanos after fixing the problems that they had | Daimon A. Boccamazzo | Not Adjusted |  | 61 | 2016-04-28 14:14 | Daimon A. Boccamazzo
273 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-26 21:04 | 702 | 165 | 8.6 |  | 230 | 262 |  | 0.83 | 4.4 | 5.8 | 0.14 | 0.1 | 0 | 0.147 | 0.81 |  | 1404470 | 169560 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 21:08 | jrojas92
274 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-26 15:06 | [26 empty] | ​water treatment loop off due to leaky copper corrosion probe, found all chem. pumps @ 100% (adjusted all to 60%), opened H-550 portafeed valve to inlet of pump, 2DT222 pump leaks, can't remove screen housing on treatment loop (too tight will use strap wrench). Will put system back online after repairs made. | dn3 | Not Adjusted |  |  | 2016-04-26 15:08 | dn3
275 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 07:23 | 677 | 166.6 | 8.2 | 205 | [8 empty] | 0.2 | [13 empty] | ​Turned on st70 for 10 min. Calibrated orp | Bob A Adams | Not Adjusted |  | 66 | 2016-03-31 07:26 | Bob A Adams
276 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-25 22:18 | 669 | 167 | 8.4 |  | 140 | 184 |  | 0.51 | 3.4 | 3.2 | 0.14 | 0 | 0.15 | 0.12 | 0.27 |  | 1392260 | 168170 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-04-27 22:26 | jrojas92
277 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-11 11:04 | 721 | 116 | 8.5 | 325 | [8 empty] | 1.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 68.1 | 2016-03-11 11:05 | Bob A Adams
278 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 14:07 | 905 | 139 | 8.3 | 220 | [8 empty] | 0 | [14 empty] | Bob A Adams | Not Adjusted |  | 62 | 2016-03-10 14:09 | Bob A Adams
279 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-05 14:14 | 691 | 99 | 8.2 | 231 | [8 empty] | 0 | [13 empty] | ​stabrex line was broken and leaking all over floor | Bob A Adams | Not Adjusted |  | 65 | 2016-02-05 14:16 | Bob A Adams
280 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 13:10 | 702 | 195.8 | 8.5 | 182 | [8 empty] | 9 | [14 empty] | Bob A Adams | Not Adjusted |  | 65 | 2015-12-31 13:14 | Bob A Adams
281 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-30 14:04 | 673 | 198 | 8.4 |  | 250 | 304 |  | 0 | 4.5 | 7.4 | 0.19 | 0 | 0.01 | 0.0892 | 0.1 |  | 1378838 | 167244 |  |  |  |  | Good | Clean | Clean | Level Okay | ​Should check ST70 pump operation, its not feeding chemical. | jrojas92 |  |  |  | 2015-12-21 14:08 | jrojas92
282 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-05 11:09 | 685 | 150.6 | 8.6 | 142 | [8 empty] | 1.9 | [13 empty] | ​ | mrh4 | Not Adjusted |  | 67.7 | 2015-11-24 11:11 | mrh4
283 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-23 14:36 | 682 | 208 | 8.6 |  | 280 | 316 |  | 0.39 | 4.8 | 9.4 | 0.13 | 0.1 | 0.02 | 0.067 | 0.06 |  | 1374110 | 166810 |  |  |  |  | Good | Clean | Clean | Level Okay | ST70 still not feeding (clogged). | jrojas92 |  |  |  | 2015-11-14 14:42 | jrojas92
284 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-23 09:59 | 691 | 147.1 | 9.3 | 131 | [8 empty] | 0 | [13 empty] | ​slug fed biocides Changed side stream filter | mrh4 | Not Adjusted |  | 68.8 | 2015-10-26 10:02 | mrh4
285 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-28 17:47 | 682 | 218 | 8.5 |  | 250 | 310 |  | 0 | 5.7 | 10.3 | 0.13 | 0 | 0.04 | 0.0526 | 0.16 |  | 1365870 | 166050 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​ST70 still appears to be clogged. Performed draw-test, but was not feeding and suction side tubing was clear/empty. | jrojas92 |  |  |  | 2015-09-30 18:07 | jrojas92
286 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-24 16:26 | 667 | 193 | 8.6 |  | 250 | 292 |  | 0.35 | 5.04 | 6.6 | 0.22 | 0.1 | 0.02 | 0.0859 | 0.82 |  | 1347950 | 164620 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​ST70 not feeding (clogged) | jrojas92 |  |  |  | 2015-11-14 16:29 | jrojas92
287 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-07-17 12:24 | 661 | 185 | 8.6 |  | 260 | 300 |  | 0.33 | 4.8 | 7.7 | 0.17 | 0 | 0 | 0.0956 | 0.34 |  | 1318700 | 162430 |  |  |  |  | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-08-18 12:40 | jrojas92
288 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-19 17:16 | 247 | 186 | 7.8 |  | 80 | 108 |  | 0 | 7 | 9.2 | 0.12 | 0.6 | 0.01 | 0.119 | 1.02 |  | 1287220 | 161220 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 17:19 | jrojas92
289 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-14 18:08 | 707 | 199 | 8.2 |  | 300 | 300 |  | 0.65 | 4.6 | 7 | 0.12 | 0.5 | 0.13 | 0.246 | 0.94 |  | 1268160 | 159760 | [7 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:11 | jrojas92
290 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-04-24 18:47 | 692 | 224 | 8.1 |  | 230 | 314 |  | 1.34 | 5 | 10.2 | 0.28 | 0 | 0.03 | 0.292 | 0.14 | [10 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:50 | jrojas92
291 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-14 13:37 | 681 | 155.5 | 8.9 | [23 empty] | Fahrenheit​ | mrh4 | Not Adjusted |  | 54.6 | 2015-09-21 13:38 | Jay Dahlstrom
292 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-27 10:16 | 683 | 161.8 | 8.7 | [9 empty] | 0 | [13 empty] | ​Fahrenheit | mrh4 | Not Adjusted |  | 53.6 | 2015-09-21 10:17 | Jay Dahlstrom
293 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-11 09:14 | 677 | 152.7 | 8.7 | [9 empty] | 0.03 | [13 empty] | ​​Fahrenheit​ | mrh4 | Not Adjusted |  | 54 | 2015-09-21 09:16 | Jay Dahlstrom
294 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-18 10:19 | 562.5 |  |  | 93 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-10-01 10:19 | RICHARD A. JOHNSON
295 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-24 09:22 | 510 |  |  | 82 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-07-30 09:23 | RICHARD A. JOHNSON
296 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-21 10:30 | 487.2 |  |  | 192 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-05-31 10:30 | RICHARD A. JOHNSON
297 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-22 07:50 | 470 |  |  | 161 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 65 | 2018-04-02 07:51 | RICHARD A. JOHNSON
298 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-28 11:26 | 620 |  |  | 214 | [8 empty] | 0.1 | [13 empty] | ​turned on st70 pump for 30mins | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2018-03-16 11:29 | Daimon A. Boccamazzo
299 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-30 13:22 | 480 |  |  | 167 | [8 empty] | 0.7 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2018-02-01 13:23 | RICHARD A. JOHNSON
300 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-22 12:13 | 460 |  |  | 154 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 73 | 2017-12-04 12:14 | RICHARD A. JOHNSON
301 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:20 | 331 |  | 9.21 | 205 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-06-19 07:21 | RICHARD A. JOHNSON
302 | 1130 | 1130-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-04 14:02 | 135 | 0 | 7.6 | [9 empty] | 0.05 |  |  |  | 500647 |  |  |  |  | Not Correct | Good | Clean | Clean | Level Okay | Trasar feed pump was found unplugged. Plugged back in and system becang pumping hcemical into the system. free chlorine was low because it was a non feed day. Conductivity probe was reading inaccurate. This has happened several times, I will be sending a new one for replacement. ​ | reedhea |  |  |  | 2017-05-04 14:07 | reedhea
303 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-24 07:36 | [26 empty] | ​didn't have any water in the chemical loop. Tower wasn't running cause of the cold weather. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-26 07:38 | Daimon A. Boccamazzo
304 | 1130 | 1130-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-12-13 14:37 | 410 | 861 | 8.1 | [9 empty] | 0.51 |  |  |  | 497363 |  |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​​Conductivity recalibrated. Trasar inhibitor manually turned off for 48 hours. Sensor overfed chemistry on 12/6 according to trends. | reedhea |  |  |  | 2016-12-13 14:41 | reedhea
305 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-06 10:18 | 358 |  | 9.2 | 146 | [8 empty] | 0.2 | [13 empty] | ​changed st70 pump speed to 60 instead of 40 | Daimon A. Boccamazzo | Up | 60 | 66 | 2016-12-12 10:22 | Daimon A. Boccamazzo
306 | 1130 | 1130-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 11:41 | 289 | 113 | 7.6 | [9 empty] | 1.15 |  |  |  | 485618 |  |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​conductivity recalibrated. | reedhea |  |  |  | 2016-11-09 12:02 | reedhea
307 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-24 14:26 | 287 |  | 9 | 230 | [8 empty] | 6.4 | [13 empty] | ​conductivity sensor needs calibration | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-10-24 14:28 | Daimon A. Boccamazzo
308 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-25 10:08 | 309 |  | 8.6 | 210 | [8 empty] | 5.5 | [13 empty] | ​check conductivity calibration' controller is 635 and my meter is reading 309. St70 high because it just got done feeding at 6 and I tested tower at 8 | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-07-26 10:11 | Daimon A. Boccamazzo
309 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:39 | 182 |  | 8.6 | 139 | [8 empty] | 0.8 | [13 empty] | ​need to check calibration on the conductivity sensor, it is reading 816 and my meter is reading 182. Otherwise system is good with no leaks or problems. Strainer is good probably should be cleaned out next time around | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2016-06-02 13:42 | Daimon A. Boccamazzo
310 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-18 13:16 | 2136 |  | 9 | 375 | [8 empty] | 2.2 | [13 empty] | ​need to check calibration on cond and orp. The controller is reading 1539 and orp is reading 549. And I got 2136 on conductivity and 375 9pm orp | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-05-18 13:19 | Daimon A. Boccamazzo
311 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 10:37 | 1085 |  | 8.9 | 228 | [8 empty] | 0.04 | [13 empty] | ​no chemicals at all in the porta feeds. Pumps not plugged in. Adjusted pump speed on all three pumps to 60. Need bucket up here as well | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-09 10:41 | Daimon A. Boccamazzo
312 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-08 14:14 | 637 | 7 | 8.4 | 330 | [8 empty] | 3 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 71 | 2016-04-08 14:15 | Bob A Adams
313 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-28 06:52 | 319 | 4 | 8.4 | 385 | [8 empty] | 4 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 68 | 2016-03-29 06:56 | Bob A Adams
314 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-11 13:59 | 630 | 8 | 8.5 | 248 | [8 empty] | 0.6 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 71.5 | 2016-03-11 14:04 | Bob A Adams
315 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-26 06:39 | 220 | 8 | 8.4 | 300 | [8 empty] | 1.8 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 70 | 2016-02-29 06:41 | Bob A Adams
316 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-23 14:25 | 71 | 0 | 8.5 | 490 | [8 empty] | 2 | [13 empty] | ​makeup water is sticking on. | Bob A Adams | Not Adjusted |  | 65 | 2016-02-23 14:26 | Bob A Adams
317 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 08:50 | 76 | 2 | 8.4 | 310 | [8 empty] | 2 | [13 empty] | ​debri from cleaning in level probe piping | Bob A Adams | Not Adjusted |  | 76 | 2016-02-08 08:52 | Bob A Adams
318 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-12 14:27 | 341 | 5 | 8.4 | 171 | [8 empty] | 0 | [13 empty] | ​Posca in range. Cleaned sensors. Blow by need to look into | Bob A Adams | Not Adjusted |  | 75 | 2016-01-12 14:36 | Bob A Adams
319 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-30 14:44 | 367 | 2 | 8.4 | 177 | [8 empty] | 0 | [13 empty] | ​​calibrated orp and turned on pump | Bob A Adams | Not Adjusted |  | 69 | 2015-12-30 14:48 | Bob A Adams
320 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-06 11:13 | 486 | 6 | 8.1 | 281 | [8 empty] | 0 | [13 empty] | ​Prime both bromine and posca pumps CH20 treatment system | mrh4 | Not Adjusted |  | 66.3 | 2015-11-24 11:17 | mrh4
321 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-08 11:09 | 631 | 8 | 8 | 215 | [8 empty] | 6 | [13 empty] | ​CH20 system. Scale inhibitor is at 8ppm this within their parameters | mrh4 | Down |  | 19.6 | 2015-10-08 11:15 | mrh4
322 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-02 14:37 | 621 | 8 | 8.2 | 221 | [8 empty] | 2 | [13 empty] | ​​Cleaned side stream filter | mrh4 | Not Adjusted |  |  | 2015-10-02 14:40 | mrh4
323 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-14 13:37 | 595 |  | 8.1 | [23 empty] | ​​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 22.3 | 2015-09-21 13:37 | Jay Dahlstrom
324 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-10 13:32 | 591 |  | 8 | [23 empty] | TEI - 6 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 23.1 | 2015-09-21 13:33 | Jay Dahlstrom
325 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-01 12:54 | 607 |  | 8.1 | [23 empty] | ​​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 25.1 | 2015-09-21 12:54 | Jay Dahlstrom
326 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-04 10:22 | 590 |  | 8 | [23 empty] | ​TEI - 3 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 27.7 | 2015-09-21 10:23 | Jay Dahlstrom
327 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-25 10:14 | 609 |  | 8.1 | [23 empty] | ​​TEI - 3 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 26.9 | 2015-09-21 10:15 | Jay Dahlstrom
328 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-20 09:21 | 627 |  | 8.1 | [23 empty] | ​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.1 | 2015-09-21 09:22 | Jay Dahlstrom
329 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-22 09:05 | 586 |  | 8.1 | [23 empty] | ​TEI - 4 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 19.4 | 2015-09-21 09:05 | Jay Dahlstrom
330 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-19 10:08 | 406.9 |  |  | 227 | [8 empty] | 0.5 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 60 | 2018-10-01 10:09 | RICHARD A. JOHNSON
331 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:32 | 561.3 |  |  | 156 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 62 | 2018-08-30 11:33 | RICHARD A. JOHNSON
332 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 10:36 | 695 |  |  | 239 | [8 empty] | 8.8 | [13 empty] | ​tower fed st70 today which is why the FC levels are so high. Everything is all good. | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2018-08-10 10:38 | Daimon A. Boccamazzo
333 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 07:03 | 629 |  |  | 206 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 62 | 2018-07-03 07:04 | RICHARD A. JOHNSON
334 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-25 13:29 | 738.5 |  |  | 230 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 59 | 2018-04-30 13:30 | RICHARD A. JOHNSON
335 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-21 10:19 | 708 |  |  | 300 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 49 | 2018-02-23 10:20 | RICHARD A. JOHNSON
336 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-29 14:04 | 675 |  |  | 270 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2017-12-29 14:05 | RICHARD A. JOHNSON
337 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-18 10:35 | 669 |  |  | 354 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2017-10-23 10:37 | RICHARD A. JOHNSON
338 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:15 | 613 |  |  | 243 | [8 empty] | 6.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2017-08-24 08:16 | RICHARD A. JOHNSON
339 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:08 | 597 |  |  | 225 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2017-08-02 10:10 | RICHARD A. JOHNSON
340 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-05-02 08:46 | 700 |  | 8.7 | 120 | [8 empty] | 0 | [13 empty] | ​everything all good. Cleaned the strainer, conductivity sensor and the flow meter. FC will feed on Wednesday so I'm not worried about the low levels today. | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2017-05-16 08:51 | Daimon A. Boccamazzo
341 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-03 11:57 | 802 |  | 8.8 | 337 | [8 empty] | 1.1 | [13 empty] | ​everything is all good | Daimon A. Boccamazzo | Not Adjusted |  | 51 | 2017-01-17 12:00 | Daimon A. Boccamazzo
342 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-28 11:03 | 780 |  | 8.3 | 335 | [8 empty] | 8.8 | [13 empty] | ​free chlorine levels high because the system had just fed st70 into the tower | Daimon A. Boccamazzo | Not Adjusted |  | 58 | 2016-11-29 11:05 | Daimon A. Boccamazzo
343 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-03 08:54 | 720 |  | 8.8 | 380 | [8 empty] | 8.8 | [13 empty] | ​tower had just fed chemical into the system that's why the free chlorine levels were so high. Other than that everything else was all good | Daimon A. Boccamazzo | Not Adjusted |  | 60 | 2016-10-14 08:56 | Daimon A. Boccamazzo
344 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-02 14:18 | 686 |  | 8.4 | 255 | [8 empty] | 8.8 | [13 empty] | ​feed 2 missed (which is the st70) but the free chlorine levels are still high. Not sure why that is? | Daimon A. Boccamazzo | Not Adjusted |  | 64 | 2016-09-06 14:21 | Daimon A. Boccamazzo
345 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-26 10:23 | 667 |  | 8.6 | 289 | [8 empty] | 0.2 | [13 empty] | ​need to find out why relay 2 keeps missing its feed. | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-07-26 10:25 | Daimon A. Boccamazzo
346 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-07 09:14 | 645 |  | 8.6 | 245 | [8 empty] | 8.8 | [13 empty] | ​free chlorine is off the charts because it he tower just got done feeding st70 for an hour. Change st70 timer to mon-wed-fri for an hour at 6am. Cleaned strainer. | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2016-06-07 09:18 | Daimon A. Boccamazzo
347 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-23 10:08 | 913 |  | 8.6 | 250 | [8 empty] | 8.8 | [13 empty] | ​free chlorine off the charts because the system just got done feeding st70 into the tower an hour ago. Strainer still looking good | Daimon A. Boccamazzo | Not Adjusted |  | 60 | 2016-05-23 10:10 | Daimon A. Boccamazzo
348 | 1223 | 1223-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-22 23:59 | 954 | 90 | 8.5 |  | 210 | 180 |  |  | 5.1 | 10.8 | 1.56 | 1.8 | 6.8 | 0.087 | 0.4 |  |  | 391200 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Turned Trasar pump back on, fluorometer is calibrated. Turned down ST70 pump from 60 to 40, because of high Cl. | jrojas92 |  |  |  | 2016-06-07 00:04 | jrojas92
349 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 10:29 | 960 |  | 8.6 | 380 | [8 empty] | 2.2 | [13 empty] | ​need bucket up here. Reasoning for the free chlorine being up so high is cause it feeds every Monday, Wednesday, and Friday at 6am for an hour and I tested the tower at 8am. Cleaned chamical loop strainer | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-09 10:35 | Daimon A. Boccamazzo
350 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-05 14:25 | [12 empty] | 8.8 | [13 empty] | ​over 8ppm. Turned st70 pump speed back down to 60. Also switched the blowdown valve back on and turned it on auto. All systems are normal | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-05 14:27 | Daimon A. Boccamazzo
351 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-05 14:23 | [12 empty] | 8.8 | [13 empty] | ​over 8 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-05 14:25 | Daimon A. Boccamazzo
352 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 14:33 | [12 empty] | 8.8 | [13 empty] | ​over 8 ppm | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 14:34 | Daimon A. Boccamazzo
353 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 09:18 | [12 empty] | 8.8 | [13 empty] | ​pumped st70 into the system for 20 minutes and turned pump speed up from 60 to 80 also turned off RO water and switched the tower to city water for make up. First test was done at 8:30am 5/4/16. second test was done at 8:32am 5/4/16. Third test was done at 8:55am 5/4/16 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 09:22 | Daimon A. Boccamazzo
354 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 09:17 | [12 empty] | 0.1 | [13 empty] | ​see third entry for notes and details | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 09:18 | Daimon A. Boccamazzo
355 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 09:16 | [12 empty] | 0.3 | [13 empty] | ​see last entry for notes and details | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 09:17 | Daimon A. Boccamazzo
356 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-03 13:16 | [12 empty] | 8.8 | [13 empty] | ​free chlorine above meter range at 8:20 am 03MAY16 & over 8 ppm again at 1:15 pm 03MAY16 | dn3 | Not Adjusted |  |  | 2016-05-03 13:19 | dn3
357 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-03 08:35 | [12 empty] | 8.8 | [13 empty] | ​Readings were off the chart because I manually pumped st70 into the system for 20 to 30 minutes. First test was at 7:47, second test was at 8:18 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-03 08:39 | Daimon A. Boccamazzo
358 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-03 08:32 | [12 empty] | 0.3 | [13 empty] | ​turned the blowdown valve off. Also pumped st70 into the system and made adjustments to the pump speed on both the st70 and the h550. Turned the pumps to 60 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-03 08:35 | Daimon A. Boccamazzo
359 | 1223 | 1223-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-27 22:38 | 868 | 2690 | 5.6 |  | 130 | 276 |  | 0.14 | 96 | 13.4 |  | 18.3 | 0.02 | 0.791 | 0.04 |  |  | 391200 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Controller was reading 390ppm, so pump turned off because of really high level until calibration. | jrojas92 |  |  |  | 2016-06-06 22:47 | jrojas92
360 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-18 12:04 | 970 |  | 6.1 | 400 | [8 empty] | 8.8 | [13 empty] | ​orp is reading a negative number, alarm for a bad sensor, also drain some water out of the tower to bring the conductivity down | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-18 12:07 | Daimon A. Boccamazzo
361 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 14:05 | 1002 | 5.9 | 8.4 | 206 | [8 empty] | 0.1 | [13 empty] | Turned on st70 for five minutes. Waiting controller to be programmed ​ | Bob A Adams | Not Adjusted |  | 60.4 | 2016-03-31 14:10 | Bob A Adams
362 | 1223 | 1223-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-28 20:37 | 401 | 0 | 8.3 |  | 150 | 74 |  | 0.5 | 0.4 | 0 | 0.4 | 0 | 0.04 | 0.288 | 0.37 |  |  | 390100 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 20:43 | jrojas92
363 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-24 09:15 | 457 | 0 | 8.4 | 303 | [8 empty] | 0.1 | [13 empty] | ​chemicals on site waiting on Nalco to turn on set up controller. | Bob A Adams | Not Adjusted |  | 56 | 2016-03-24 09:17 | Bob A Adams
364 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 10:26 | 761 | 0 | 8.6 | 216 | [8 empty] | 0 | [13 empty] | ​Waiting for Nalco to deliver Chema. | Bob A Adams | Not Adjusted |  | 61 | 2016-03-10 10:29 | Bob A Adams
365 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-09 07:41 | 587 | 6 | 8.5 | 214 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Cleaned sensors. Last time testing with H2O. | Bob A Adams | Not Adjusted |  | 58.5 | 2016-02-09 07:46 | Bob A Adams
366 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-26 14:04 | 625 | 10 | 8.4 | 237 | [8 empty] | 0.8 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 58 | 2016-01-28 14:06 | Bob A Adams
367 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-14 06:51 | 673 | 10 | 8.7 | 350 | [8 empty] | 2 | [13 empty] | ​Posca in range. Cleaned Sensors. Calibrated conductivity and orp | Bob A Adams | Not Adjusted |  | 55 | 2016-01-14 06:54 | Bob A Adams
368 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-05 07:43 | 628 | 8 | 8.7 | 338 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Calibrated conductivity. Cleaned sensors | Bob A Adams | Not Adjusted |  | 54 | 2016-01-05 07:45 | Bob A Adams
369 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:34 | 640 | 6 | 8.6 | 241 | [8 empty] | 0.9 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 62 | 2015-12-31 07:38 | Bob A Adams
370 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 06:47 | 626 | 6 | 8.7 | 230 | [8 empty] | 1.8 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 61.2 | 2015-12-09 06:50 | Bob A Adams
371 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-02 06:54 | 624 | 8 | 8.6 | 269 | [8 empty] | 0.7 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 71 | 2015-12-04 06:58 | Bob A Adams
372 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-23 14:14 | 606 | 8 | 8.6 | 312 | [8 empty] | 1.3 | [13 empty] | ​​cleaned sensors. Posca in range | Bob A Adams | Not Adjusted |  | 66 | 2015-11-30 14:17 | Bob A Adams
373 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-12 13:47 | 604 | 6 | 8.5 | 360 | [8 empty] | 2 | [13 empty] | ​Posca is in range | Bob A Adams | Not Adjusted |  | 56.8 | 2015-11-16 13:50 | Bob A Adams
374 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-28 06:55 | 658 | 8 | 8.8 | 133 | [8 empty] | 0.3 | [13 empty] | ​Free chlorine and Posca in range | Bob A Adams | Not Adjusted |  | 63.2 | 2015-11-03 06:58 | Bob A Adams
375 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-27 14:24 | 602 | 10 | 8.6 | 262 | [8 empty] | 0.4 | [13 empty] | Posca and conductivity in range ​ | Bob A Adams | Not Adjusted |  | 60 | 2015-10-28 14:28 | Bob A Adams
376 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-09 08:19 | 583 | 4 | 8.5 | 300 | [8 empty] | 1.2 | [13 empty] | ​Posca and conductivity in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 65.7 | 2015-10-26 08:22 | Bob A Adams
377 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-25 12:28 | 588 |  | 8.6 | [23 empty] | ​ORP= 319 TWO= 1.9 OP= 6 | mrh4 | Not Adjusted |  | 65.6 | 2015-09-21 12:29 | Cesar Escobar
378 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-18 12:27 | 610 |  | 8.5 | [23 empty] | ​ORP= 290 TWO= .7 OP= 6 | mrh4 | Not Adjusted |  | 67 | 2015-09-21 12:28 | Cesar Escobar
379 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-11 12:26 | 547 |  | 8.6 | [23 empty] | ​ | mrh4 | Not Adjusted |  | 66.7 | 2015-09-21 12:27 | Cesar Escobar
380 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-04 12:25 | 665 |  | 8.5 | [23 empty] | ​ORP= 174 TWO= 0.1 OP= 8 | mrh4 | Not Adjusted |  | 63.3 | 2015-09-21 12:26 | Cesar Escobar
381 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-30 12:24 | 641 |  | 8.5 | [23 empty] | ​ORP= 238 TWO= .5 OP= 6 | mrh4 | Not Adjusted |  | 65.5 | 2015-09-21 12:24 | Cesar Escobar
382 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-05 12:22 | 584 |  | 8.5 | [23 empty] | ​ORP= 230 TWO= .4 OP= 6 | mrh4 | Not Adjusted |  | 60.1 | 2015-09-21 12:23 | Cesar Escobar
383 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-01 12:19 | 614 |  | 8.4 | [23 empty] | ​ORP= 245 TWO= .2 OP= 6 | mrh4 | Not Adjusted |  | 62.3 | 2015-09-21 12:22 | Cesar Escobar
384 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-19 12:07 | 590 |  | 8.5 | [23 empty] | ORP= 265 TWO= .4​ OP= 4 | mrh4 | Not Adjusted |  | 61.7 | 2015-09-21 12:19 | Cesar Escobar
385 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-12 12:06 | 565 |  | 8.4 | [23 empty] | ​ORP= 255 TWO= .9 OP= 10 | mrh4 | Not Adjusted |  | 61 | 2015-09-21 12:07 | Cesar Escobar
386 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-07 12:04 | 569 |  | 8.4 | [23 empty] | ​ORP= 271 TWO= .6 OP= 8 | mrh4 | Not Adjusted |  | 58.2 | 2015-09-21 12:05 | Cesar Escobar
387 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-06 12:03 | 579 |  | 8.5 | [23 empty] | ​ORP= 210 TWO= 0 OP= 8 | mrh4 | Not Adjusted |  | 57.9 | 2015-09-21 12:04 | Cesar Escobar
388 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-04 12:02 | 586 |  | 8.2 | [23 empty] | ​ORP= 202 TWO= 0 OP= 6 | mrh4 | Not Adjusted |  | 58 | 2015-09-21 12:03 | Cesar Escobar
389 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-23 12:01 | 612 |  | 8.6 | [23 empty] | ​ORP= 267 TWO= 0 OP= 6 | mrh4 | Not Adjusted |  | 57.4 | 2015-09-21 12:02 | Cesar Escobar
390 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 12:00 | 628 |  | 8.6 | [23 empty] | ​ORP= 295 TWO= .9 OP= 8 | mrh4 | Not Adjusted |  | 56.5 | 2015-09-21 12:01 | Cesar Escobar
391 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-21 11:59 | 575 |  | 8.4 | [23 empty] | ​ORP= 306 TWO= 2.1 OP= 4 | mrh4 | Not Adjusted |  | 60.6 | 2015-09-21 12:00 | Cesar Escobar
392 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 11:58 | 585 |  | 8.4 | [23 empty] | ​ORP= 305 TWO= 1.8 OP= 6 | mrh4 | Not Adjusted |  | 58.5 | 2015-09-21 11:59 | Cesar Escobar
393 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-16 13:52 | 557 |  | 7.9 | [23 empty] | ​TEI - 2 ppm POSCA - 10 ppm | mrh4 | Not Adjusted |  | 11.7 | 2015-09-21 13:53 | Jay Dahlstrom
394 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-09 11:57 | 607 |  | 8.5 | [23 empty] | ​TWO= 2.1 OP= 8 | mrh4 | Not Adjusted |  | 59.3 | 2015-09-21 11:58 | Cesar Escobar
395 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-17 11:56 | 622 |  | 8.5 | [23 empty] | ​ORP= 258 TWO= .6 OP= 8 | mrh4 | Not Adjusted |  | 60.5 | 2015-09-21 11:57 | Cesar Escobar
396 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-13 11:55 | 620 |  | 8.6 | [23 empty] | ​ORP= 244 TWO= 1.1 OP= 8 | mrh4 | Not Adjusted |  | 61.1 | 2015-09-21 11:56 | Cesar Escobar
397 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-11 11:54 | 628 |  | 8.5 | [23 empty] | ORP= 248 TWO= 1.2 OP= 6​ | mrh4 | Not Adjusted |  | 60.2 | 2015-09-21 11:55 | Cesar Escobar
398 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-05 11:53 | 600 |  | 8.6 | [23 empty] | ​ORP= 281 TWO= .8 OP= 8 | mrh4 | Not Adjusted |  | 55 | 2015-09-21 11:54 | Cesar Escobar
399 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-03 11:52 | 609 |  | 8.5 | [23 empty] | ​ORP= 280 TWO= .6 OP= 8 | mrh4 | Not Adjusted |  | 56.8 | 2015-09-21 11:52 | Cesar Escobar
400 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-26 11:51 | 629 |  | 8.1 | [23 empty] | ​ORP= 282 TWO= .5 OP= 8 | mrh4 | Not Adjusted |  | 56.7 | 2015-09-21 11:52 | Cesar Escobar
401 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-23 11:49 | 615 |  | 8.3 | [23 empty] | ​ORP= 269 TWO= .4 OP= 8 | mrh4 | Not Adjusted |  | 57.2 | 2015-09-21 11:50 | Cesar Escobar
402 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-18 11:48 | 605 |  | 8.4 | [23 empty] | ​ORP= 278 TWO= .8 OP= 10 | mrh4 | Not Adjusted |  | 56.9 | 2015-09-21 11:49 | Cesar Escobar
403 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-10 11:35 | 552 |  | 8.4 | [23 empty] | ​ORP= 337 TWO= 1.9 OP= 8 | mrh4 | Not Adjusted |  | 60.9 | 2015-09-21 11:48 | Cesar Escobar
404 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-05 11:34 | 635 |  | 8.5 | [23 empty] | ​ORP= 237 TWO= 1.4 OP= 10 | mrh4 | Not Adjusted |  | 59.9 | 2015-09-21 11:35 | Cesar Escobar
405 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-27 11:32 | 638 |  | 8.6 | [23 empty] | ​ORP= 260 TWO= 2.6 OP= 8 | mrh4 | Not Adjusted |  | 60.7 | 2015-09-21 11:34 | Cesar Escobar
406 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-21 11:30 | 653 |  | 8.3 | [23 empty] | ​ORP= 380 OP= 8 | mrh4 | Not Adjusted |  | 54.2 | 2015-09-21 11:31 | Cesar Escobar
407 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-13 11:29 | 618 |  | 8.2 | [23 empty] | ​ORP= 331 TWO= 1.2 OP= 10 | mrh4 | Not Adjusted |  | 55.6 | 2015-09-21 11:30 | Cesar Escobar
408 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-08 11:27 | 591 |  | 8.6 | [23 empty] | ​ORP= 250 TWO= 1.5 OP= 8 | mrh4 | Not Adjusted |  | 56.2 | 2015-09-21 11:29 | Cesar Escobar
409 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-05 11:24 | 536 | [25 empty] | ​​ORP= 270 TWO= .1 OP= 8 | mrh4 | Not Adjusted |  | 60.8 | 2015-09-21 11:26 | Cesar Escobar
410 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-19 10:11 | 1840 |  |  | 218 | [8 empty] | 3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2018-10-01 10:12 | RICHARD A. JOHNSON
411 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:37 | 1806 |  |  | 147 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2018-08-30 11:37 | RICHARD A. JOHNSON
412 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 10:47 | 1610 |  |  | 249 | [8 empty] | 0.7 | [13 empty] | ​tried to let some water run through the chemical loop and clean it out. Also cleaned the strainer and conductivity probe. | Daimon A. Boccamazzo | Not Adjusted |  | 78 | 2018-08-10 10:50 | Daimon A. Boccamazzo
413 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 07:01 | 1394 |  |  | 200 | [8 empty] | 1.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-07-03 07:02 | RICHARD A. JOHNSON
414 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-23 13:22 | 951 |  |  | 161 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 73.5 | 2018-04-30 13:23 | RICHARD A. JOHNSON
415 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-20 10:15 | 325 |  |  | 179 | [8 empty] | 0.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-02-23 10:15 | RICHARD A. JOHNSON
416 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-27 13:55 | 328 |  |  | 206 | [8 empty] | 0.5 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-12-29 13:56 | RICHARD A. JOHNSON
417 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-20 10:43 | 1520 |  |  | 223 | [8 empty] | 0.7 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2017-10-23 10:44 | RICHARD A. JOHNSON
418 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:19 | 679 |  |  | 207 | [8 empty] | 0.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-08-24 08:20 | RICHARD A. JOHNSON
419 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:06 | 626 |  |  | 240 | [8 empty] | 0.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-02 10:08 | RICHARD A. JOHNSON
420 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-05 13:04 | 450 |  | 8.9 | 176 | [8 empty] | 2.6 | [13 empty] | ​​low conductivity due to tower not running as frequently anymore because there is no demand for it in the cold weather | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2017-01-17 13:07 | Daimon A. Boccamazzo
421 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-28 11:16 | 330 |  | 9 | 375 | [8 empty] | 8.8 | [13 empty] | ​free chlorine high because the system had just fed st70 into the tower. Conductivity sensor needs calibration | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-11-29 11:24 | Daimon A. Boccamazzo
422 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-04 09:02 | 210 |  | 9.4 | 180 | [8 empty] | 0.2 | [13 empty] | ​free chlorine low because I tested the tower in between the towers fed cycle. Conductivity sensor needs to be calibrated, it is reading 439 and my meter is reading 210. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-10-14 09:06 | Daimon A. Boccamazzo
423 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-02 14:27 | 554 |  | 8.9 | 200 | [8 empty] | 3.6 | [13 empty] | ​st70 had just feed and that's why chlorine levels are so high, and cleaned strainer | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-09-06 14:30 | Daimon A. Boccamazzo
424 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-26 10:28 | 108 |  | 9.3 | 250 | [8 empty] | 1.5 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Need to check calibration on conductivity sensor, reading at 325 and my meter is reading 108 | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-07-26 10:32 | Daimon A. Boccamazzo
425 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-29 11:47 | 612 |  | 8.8 | 200 | [8 empty] | 4 | [13 empty] | ​cleaned strainer, flow sensor, and conductivity sensor. Changed st70 timer to 1 hour every mon, wed, and fri At 12. Also put a timer on the h-550 for 30 minutes every Sunday at 1. The calibration might need to be checked on the conductivity sensor, it's reading 850 and my meter is reading about 615 | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-06-29 11:52 | Daimon A. Boccamazzo
426 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-24 14:48 | 557 |  | 8.8 | 280 | [8 empty] | 4.4 | [13 empty] | ​turned pump speed down to 60. Need to check calibration on conductivity sensor, it is reading 814 and my meter is reading 557. Cleaned strainer. Did visual check on tower as well and it looks good no leaks or problems | Daimon A. Boccamazzo | Down | 60 | 70 | 2016-05-24 15:01 | Daimon A. Boccamazzo
427 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 12:12 | 547 |  | 8.8 | 245 | [8 empty] | 0.42 | [13 empty] | ​check calibration on the controller, it is reading 743 and my conductivity meter is reading 547. I cleaned flow sensor and chemical loop strainer. There is a good amount of chemical in each bucket | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-05-10 12:17 | Daimon A. Boccamazzo
428 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-20 12:20 | 545 |  | 8.3 | 250 | [8 empty] | 7.8 | [13 empty] | ​​tested the tower for free chlorine and it was a pretty high but the best reasoning for that was because I tested it 20 minutes after they cycled through the Chemical, the cycling time is Monday, Wednesday, and Friday at 12. Also cleaned the chemical loop screen | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-20 12:26 | Daimon A. Boccamazzo
429 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-01 13:59 | 544 | 0 | 8.5 | 781 | [8 empty] | 5 | [13 empty] | ​Controller not programmed. Two chemicals not pumping | Bob A Adams | Not Adjusted |  | 76 | 2016-04-01 14:03 | Bob A Adams
430 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-24 11:03 | 110 | 0 | 8.4 | 235 | [8 empty] | 0.1 | [13 empty] | ​Nalco has not set up controller . | Bob A Adams | Not Adjusted |  | 70.3 | 2016-03-24 11:10 | Bob A Adams
431 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-16 14:08 | 321 | 1 | 8.3 | 218 | [8 empty] | 0.8 | [13 empty] | ​will be on Nalco for next test | Bob A Adams | Not Adjusted |  | 68.8 | 2016-03-16 14:10 | Bob A Adams
432 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-08 06:46 | 763 | 7 | 8.3 | 483 | [8 empty] | 5 | [13 empty] | ​posca in range. Orp sensor needed calibration. | Bob A Adams | Not Adjusted |  | 70 | 2016-03-08 06:49 | Bob A Adams
433 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-26 06:35 | 746 | 6 | 8.5 | 305 | [8 empty] | 1.4 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 65 | 2016-02-29 06:38 | Bob A Adams
434 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-25 13:54 | 563 | 8 | 8.5 | 269 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Cleaned sensors. | Bob A Adams | Not Adjusted |  | 67 | 2016-01-25 13:55 | Bob A Adams
435 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-12 07:02 | 288 | 4 | 8.4 | 162 | [8 empty] | 0 | [13 empty] | ​Posca in range. Cleaned sensors. Calibrated orp. Pump lost prime | Bob A Adams | Not Adjusted |  | 72 | 2016-01-12 07:04 | Bob A Adams
436 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-05 11:03 | 245 | 2 | 8.5 | 314 | [8 empty] | 0 | [13 empty] | ​There was no water coming out of f drain line. Leak in loop must be increasing | Bob A Adams | Not Adjusted |  | 71.4 | 2016-01-05 11:06 | Bob A Adams
437 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 06:40 | 606 | 2 | 8.6 | 252 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 66.8 | 2015-12-09 06:44 | Bob A Adams
438 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-01 06:49 | 610 | 6 | 8.5 | 315 | [8 empty] | 1.2 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 56 | 2015-12-04 06:52 | Bob A Adams
439 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-30 13:53 | 418 | 6 | 8.5 | 286 | [8 empty] | 0.8 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 69 | 2015-11-30 13:55 | Bob A Adams
440 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-12 13:53 | 591 | 6 | 8.5 | 330 | [8 empty] | 1.4 | [13 empty] | ​Posca in range. Cleaned the sensors | Bob A Adams | Not Adjusted |  | 71 | 2015-11-16 13:56 | Bob A Adams
441 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-06 14:16 | 574 | 4 | 8.5 | 370 | [8 empty] | 2 | [13 empty] | Posca and conductivity in range. Cleaned sensors ans set time.​ | Bob A Adams | Not Adjusted |  | 74 | 2015-11-06 14:22 | Bob A Adams
442 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-27 14:35 | 587 | 8 | 8.5 | 289 | [8 empty] | 0.8 | [14 empty] | Bob A Adams | Not Adjusted |  | 68 | 2015-10-28 14:37 | Bob A Adams
443 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-20 08:45 | 599 |  | 8.5 | [23 empty] | ​​ORP = 281 TWO = 0.6 OP = 6 | mrh4 | Not Adjusted |  | 71 | 2015-09-24 08:46 | Marilyn Fick
444 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-20 08:41 | 599 |  | 8.5 | [23 empty] | ​ORP = 277 TWO = 1.5 OP = 6 | mrh4 | Not Adjusted |  | 71 | 2015-09-24 08:42 | Marilyn Fick
445 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-12 08:40 | 584 |  | 8.5 | [23 empty] | ​ORP = 277 TWO = 1.5 OP = 6 | mrh4 | Not Adjusted |  | 70 | 2015-09-24 08:41 | Marilyn Fick
446 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-10 08:40 | [26 empty] | ​OUT OF BROMINE, REPLACED & CLEANED SENSORS​ | mrh4 | Not Adjusted |  |  | 2015-09-24 08:40 | Marilyn Fick
447 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-06 08:38 | 587 |  | 8.5 | [23 empty] | ​ORP = 270 TWO = 1.5 OP = 4 | mrh4 | Not Adjusted |  | 72.1 | 2015-09-24 08:40 | Marilyn Fick
448 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-04 08:37 | 616 |  | 8.5 | [23 empty] | ​ORP = 255 TWO = 1.9 OP = 6 | mrh4 | Not Adjusted |  | 70.7 | 2015-09-24 08:38 | Marilyn Fick
449 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-24 08:36 | 573 |  | 8.6 | [23 empty] | ​ORP = 275 TWO = 1.2 OP = 4 REPLACED POSCA, ON FOR 10 MIN | mrh4 | Not Adjusted |  | 74.8 | 2015-09-24 08:37 | Marilyn Fick
450 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-23 08:35 | [26 empty] | ​BROMINE PUMPING CLEANED SENSORS | mrh4 | Not Adjusted |  |  | 2015-09-24 08:36 | Marilyn Fick
451 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-01 08:34 | 597 |  | 8.5 | [23 empty] | ​ORP = 312​ TWO = 1.0 OP = 2 POSCA ON 10 MIN | mrh4 | Not Adjusted |  | 73.2 | 2015-09-24 08:35 | Marilyn Fick
452 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-18 08:33 | 580 |  | 8.4 | [23 empty] | ​​ORP = 320 TWO = 0.7 OP = 4 PRIMED POSCA | mrh4 | Not Adjusted |  | 71.3 | 2015-09-24 08:34 | Marilyn Fick
453 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-12 08:32 | 586 |  | 8.5 | [23 empty] | ​ORP = 315 TWO = 1.2 OP = 6 | mrh4 | Not Adjusted |  | 73.6 | 2015-09-24 08:33 | Marilyn Fick
454 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-29 08:30 | 586 |  | 8.5 | [23 empty] | ​ORP = 324 TWO = 1.5 OP = 2 POSCA 10 ON | mrh4 | Not Adjusted |  | 69.7 | 2015-09-24 08:32 | Marilyn Fick
455 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 08:29 | 637 |  | 8.6 | [23 empty] | ​ORP = 72 TWO = 0 OP = 4 | mrh4 | Not Adjusted |  | 72.2 | 2015-09-24 08:30 | Marilyn Fick
456 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 08:28 | 623 |  | 8.5 | [23 empty] | ​ORP = 70 TWO = 0 OP = 6 | mrh4 | Not Adjusted |  | 69.4 | 2015-09-24 08:28 | Marilyn Fick
457 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-16 13:53 | 573 |  | 7.9 | [23 empty] | TEI - 0 ppm ​POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.5 | 2015-09-21 13:54 | Jay Dahlstrom
458 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-07 08:26 | 639 |  | 8 | [23 empty] | ​ORP = 190 TWO = 0.2 OP = 2 POSCA ON 10 MIN | mrh4 | Not Adjusted |  | 70 | 2015-09-24 08:27 | Marilyn Fick
459 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-07 08:20 | 639 |  | 8 | [23 empty] | ​ORP = 325 TWO = 1.1 OP = 2 | mrh4 | Not Adjusted |  | 70 | 2015-09-24 08:20 | Marilyn Fick
460 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-02 08:11 | 611 |  | 8 | [23 empty] | ​ORP = 325 TWO = 1.1 OP = 2 | mrh4 | Not Adjusted |  | 71 | 2015-09-24 08:20 | Marilyn Fick
461 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-26 08:10 | 447 |  | 7.8 | [23 empty] | ​ORP = 345​ TWO = 1.8 OP = 4 | mrh4 | Not Adjusted |  | 71.2 | 2015-09-24 08:11 | Marilyn Fick
462 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-04 08:09 | 370 |  | 8.5 | [23 empty] | ​ORP = 373 TWO = 2.1 OP = 2 | mrh4 | Not Adjusted |  | 54.6 | 2015-09-24 08:10 | Marilyn Fick
463 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-02 08:08 | 345 |  | 8.4 | [23 empty] | ​ORP = 340 TWO = 1.9 OP = 4 | mrh4 | Not Adjusted |  | 55.1 | 2015-09-24 08:09 | Marilyn Fick
464 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-18 08:07 | 437 |  | 8.4 | [23 empty] | ​​ORP = 212 TWO = 0.4 OP = 6 | mrh4 | Not Adjusted |  | 61.2 | 2015-09-24 08:08 | Marilyn Fick
465 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-10 08:06 | 585 |  | 8.5 | [23 empty] | ​ORP = 298 TWO = 0.8 OP = 6 | mrh4 | Not Adjusted |  | 69.8 | 2015-09-24 08:07 | Marilyn Fick
466 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-28 08:05 | 570 |  | 8.6 | [23 empty] | ​ORP = 350 TWO = 1.6 OP = 6​ POSCA 60-65 | mrh4 | Not Adjusted |  | 70.6 | 2015-09-24 08:06 | Marilyn Fick
467 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-21 08:01 | 614 |  | 8.4 | [23 empty] | ​ORP = 331 TWO = 1.5 OP = 2 | mrh4 | Not Adjusted |  | 70.2 | 2015-09-24 08:05 | Marilyn Fick
468 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-05 08:00 | 619 |  | 8.6 | [23 empty] | ​ORP = 314 TWO = 1.5​ OP = 8 | mrh4 | Not Adjusted |  | 71 | 2015-09-24 08:01 | Marilyn Fick
469 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-22 06:50 | 245 | 0 | 8.1 | 227 | [8 empty] | 0.1 | [14 empty] | Bob A Adams | Not Adjusted |  | 71.4 | 2016-02-22 07:02 | Bob A Adams
470 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-19 12:47 | 214 | 0 | 8.3 | 705 | [8 empty] | 23 | [13 empty] | ​Bleed for 10 minutes | Bob A Adams | Not Adjusted |  | 74.3 | 2016-02-19 12:49 | Bob A Adams
471 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-19 11:13 | 237 | 0 | 8 | 730 | [8 empty] | 30 | [13 empty] | ​bleed and retesting in 2 hrs | Bob A Adams | Not Adjusted |  | 72.7 | 2016-02-19 11:15 | Bob A Adams
472 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-19 09:51 | 265 | 0 | 8.1 | 724 | [8 empty] | 42 | [13 empty] | ​bleed for 10 minutes | Bob A Adams | Not Adjusted |  | 75.1 | 2016-02-19 09:53 | Bob A Adams
473 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-18 14:18 | 183 | 0 | 8.4 | 678 | [8 empty] | 32 | [13 empty] | Will monitor and retest in 30 minutes ​ | Bob A Adams | Not Adjusted |  | 72.2 | 2016-02-18 14:20 | Bob A Adams
474 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-18 13:25 | 170 | 0 | 8.3 | 690 | [8 empty] | 35 | [13 empty] | ​will wait until 2:30 and test again | Bob A Adams | Not Adjusted |  | 71.5 | 2016-02-18 13:27 | Bob A Adams
475 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-18 11:57 | 760 | 0 | 8.4 | 712 | [8 empty] | 80 | [13 empty] | ​Free chlorine was 80 plus. Bleeding and retesting | Bob A Adams | Not Adjusted |  | 67 | 2016-02-18 11:58 | Bob A Adams
476 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-18 11:55 | 1435 | 0 | 8.7 | 710 | [8 empty] | 80 | [13 empty] | ​Free chlorine was 80 plus. Bleeding and retesting | Bob A Adams | Not Adjusted |  | 69.3 | 2016-02-18 11:57 | Bob A Adams
477 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-18 11:52 | 2637 | 0 | 9 | 675 | [8 empty] | 80 | [13 empty] | ​Free chlorine is plus 80. Bleeding and retesting | Bob A Adams | Not Adjusted |  | 72.2 | 2016-02-18 11:55 | Bob A Adams
478 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-11 08:21 | 354 | 4 | 8.5 | 147 | [8 empty] | 0 | [13 empty] | ​Posca in range. Put new bag of pellets in feeder. | Bob A Adams | Not Adjusted |  | 73 | 2016-02-12 08:25 | Bob A Adams
479 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-15 14:05 | 644 | 8 | 8.4 | 225 | [8 empty] | 0.2 | [13 empty] | ​Posca in range. Tower is building conductivity after fixing soliniod valve leak | Bob A Adams | Not Adjusted |  | 74 | 2016-01-15 14:07 | Bob A Adams
480 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-05 11:06 | 157 | 3 | 8.3 | 218 | [8 empty] | 0.1 | [13 empty] | ​no water draining. Wondering if city water valve is properly closed in basement mechanical room | Bob A Adams | Not Adjusted |  | 74 | 2016-01-05 11:10 | Bob A Adams
481 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:44 | 521 | 6 | 8.3 | 231 | [8 empty] | 0.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 69 | 2015-12-31 07:46 | Bob A Adams
482 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-06 14:25 | 651 | 6 | 8.4 | 351 | [8 empty] | 0.1 | [13 empty] | ​Posca in range. | Bob A Adams | Not Adjusted |  | 70.9 | 2015-11-06 14:28 | Bob A Adams
483 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-28 07:04 | 605 | 16 | 8.4 | 315 | [8 empty] | 0.1 | [13 empty] | ​ | Bob A Adams | Not Adjusted |  | 65 | 2015-11-03 07:06 | Bob A Adams
484 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-01 14:08 | 186 | 4 | 8.5 | 235 | [8 empty] | 1.3 | [13 empty] | ​Posca in range. Tower leaks and makes up a lot of water. | Bob A Adams | Not Adjusted |  | 68.1 | 2015-10-01 14:13 | Bob A Adams
485 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-17 13:55 | 533 |  | 7.7 | [23 empty] | TEI - 2 ppm POSCA - 10 ppm​ | mrh4 | Not Adjusted |  | 19.7 | 2015-09-21 13:56 | Jay Dahlstrom
486 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-15 13:42 | 884 |  | 8.1 | [23 empty] | TEI - 1 ppm POSCA - 20+ ppm​ | mrh4 | Not Adjusted |  | 22.9 | 2015-09-21 13:43 | Jay Dahlstrom
487 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-09-24 10:13 | 861 |  |  | 218 | [8 empty] | 8.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 82 | 2018-10-01 10:14 | RICHARD A. JOHNSON
488 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-08-23 11:38 | 778.3 |  |  | 112 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2018-08-30 11:39 | RICHARD A. JOHNSON
489 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2018-08-23 11:38 | 801.6 |  |  | 121 | [8 empty] | 7.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-08-30 11:38 | RICHARD A. JOHNSON
490 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-07-31 10:53 | 736 |  |  | 185 | [8 empty] | 0 | [13 empty] | ​cleaned strainer and fed st70 into the system to bring the FC levels up. | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2018-08-10 10:55 | Daimon A. Boccamazzo
491 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2018-07-31 10:50 | 841 |  |  | 191 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer. System started feeding st70 after I was done testing it. | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2018-08-10 10:52 | Daimon A. Boccamazzo
492 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-06-29 07:00 | 828.4 |  |  | 208 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2018-07-03 07:00 | RICHARD A. JOHNSON
493 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2018-06-29 06:59 | 875.9 |  |  | 229 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2018-07-03 06:59 | RICHARD A. JOHNSON
494 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-04-23 13:25 | 588.1 |  |  | 268 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2018-04-30 13:26 | RICHARD A. JOHNSON
495 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-02-22 10:14 | 2829 |  |  | 93 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 49 | 2018-02-23 10:14 | RICHARD A. JOHNSON
496 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2018-02-22 10:13 | 2299 |  |  | 94 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 47 | 2018-02-23 10:13 | RICHARD A. JOHNSON
497 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-12-29 14:02 | 2735 |  |  | 114 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2017-12-29 14:02 | RICHARD A. JOHNSON
498 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2017-12-29 14:01 | 3099 |  |  | 210 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 55 | 2017-12-29 14:02 | RICHARD A. JOHNSON
499 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-10-20 10:47 | 844 |  |  | 253 | [8 empty] | 4.8 | [13 empty] | ​ | RICHARD A. JOHNSON | Not Adjusted |  | 64 | 2017-10-23 10:48 | RICHARD A. JOHNSON
500 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2017-10-20 10:45 | 761 |  |  | 265 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 64 | 2017-10-23 10:46 | RICHARD A. JOHNSON
501 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-08-24 08:33 | 918 |  |  | 340 | [8 empty] | 5.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-08-24 08:34 | RICHARD A. JOHNSON
502 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2017-08-24 08:31 | 808 |  |  | 296 | [8 empty] | 7.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-08-24 08:33 | RICHARD A. JOHNSON
503 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-08-02 10:04 | 829 |  |  | 210 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 75 | 2017-08-02 10:06 | RICHARD A. JOHNSON
504 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2017-08-02 10:03 | 737 |  |  | 132 | [8 empty] | 0.2 | [13 empty] | ​tested on off day | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2017-08-02 10:04 | RICHARD A. JOHNSON
505 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-01-05 13:11 | 2675 |  | 8.9 | 194 | [8 empty] | 0.2 | [13 empty] | ​testing tower before putting it in winter mode. Fed st70 in the system for 30 mins to bring the free chlorine levels up before shutting the tower down | Daimon A. Boccamazzo | Not Adjusted |  | 43 | 2017-01-17 13:15 | Daimon A. Boccamazzo
506 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2017-01-05 13:08 | 1370 |  | 8.9 | 198 | [8 empty] | 1.3 | [13 empty] | ​​testing the tower before putting it in winter mode | Daimon A. Boccamazzo | Not Adjusted |  | 42 | 2017-01-17 13:10 | Daimon A. Boccamazzo
507 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-11-29 11:33 | 1512 |  | 8.5 | 174 | [8 empty] | 0.2 | [13 empty] | ​conductivity probe needs calibration. Probe is reading 1282 | Daimon A. Boccamazzo | Not Adjusted |  | 58 | 2016-11-29 11:35 | Daimon A. Boccamazzo
508 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-11-29 11:28 | 862 |  | 8.4 | 185 | [8 empty] | 0.3 | [13 empty] | ​adjusted st70 pump from 40 to 60 | Daimon A. Boccamazzo | Up | 60 | 56 | 2016-11-29 11:32 | Daimon A. Boccamazzo
509 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-10-04 09:09 | 693 |  | 9.1 | 287 | [8 empty] | 0 | [13 empty] | ​​turned st70 pump to 80% instead of 60% because tower just isn't getting enough chemical pumping at that speed with how little the feeding time frame is. Also fixed a leak on the h-550 pump | Daimon A. Boccamazzo | Up | 80 | 75 | 2016-10-14 09:12 | Daimon A. Boccamazzo
510 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-10-04 09:07 | 763 |  | 9 | 230 | [8 empty] | 2.1 | [14 empty] | Daimon A. Boccamazzo | Not Adjusted |  | 63 | 2016-10-14 09:09 | Daimon A. Boccamazzo
511 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-09-06 14:35 | 1026 |  | 8.8 | 142 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Free chlorine levels low because I tested on Tuesday and the system feeds every Monday, Wednesday, and friday | Daimon A. Boccamazzo | Up | 60 | 67 | 2016-09-06 14:38 | Daimon A. Boccamazzo
512 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-09-06 14:32 | 779 |  | 8.6 | 135 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer, flow and conductivity sensors, free chlorine levels so low because I tested on Tuesday and the system feeds on modal, Wednesday, and Friday | Daimon A. Boccamazzo | Up | 60 | 61 | 2016-09-06 14:35 | Daimon A. Boccamazzo
513 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-07-28 13:51 | 701 |  | 8.8 | 196 | [8 empty] | 0.1 | [13 empty] | ​strainer is good just need to find out how to change the timer on the st70 | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2016-07-29 13:55 | Daimon A. Boccamazzo
514 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-07-28 13:46 | 790 |  | 8.7 | 140 | [8 empty] | 4.6 | [13 empty] | ​cleaned conductivity sensor and strainer. Need to get corrosion probe checked, alarm on #2 probe | Daimon A. Boccamazzo | Not Adjusted |  | 71 | 2016-07-29 13:51 | Daimon A. Boccamazzo
515 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-06-29 11:55 | 722 |  | 8.9 | 261 | [8 empty] | 2.7 | [13 empty] | ​cleaned strainer, flow sensor, and conductivity sensor. No problems everything in check | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-06-29 11:57 | Daimon A. Boccamazzo
516 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-06-29 11:52 | 742 |  | 8.9 | 272 | [8 empty] | 4.8 | [13 empty] | ​cleaned strainer, flow sensor, and conductivity sensor. They will definitely need to be cleaned next time around if they are as bad as they were today | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-06-29 11:55 | Daimon A. Boccamazzo
517 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-05-24 11:49 | 685 |  | 8.8 | 170 | [8 empty] | 0.5 | [13 empty] | ​strainer is good. Checked both towers and they both look good with no problems or leaks also conductivity sensor was calibrated on tower 1 | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-05-26 11:54 | Daimon A. Boccamazzo
518 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-05-24 11:44 | 798 |  | 8.9 | 160 | [8 empty] | 0.3 | [13 empty] | ​need to find out and label which relay is which. Would like to change the time settings on the st70. Cleaned strainer. | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-05-26 11:49 | Daimon A. Boccamazzo
519 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2016-05-22 23:52 | 670 | 372 | 8.6 |  | 220 | 182 |  |  | 0.9 | 14.2 | 1.02 | 15 | 1.31 | 0.106 | 0.13 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​Connected corrosion probes to controller. | jrojas92 |  |  |  | 2016-06-06 23:54 | jrojas92
520 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-22 23:46 | 871 | 130 | 8.6 |  | 250 | 260 |  |  | 0.8 | 4.5 | 0.3 | 0 | 0.83 | 0.095 | 0.1 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​Calibrated conductivity, 2-point. | jrojas92 |  |  |  | 2016-06-06 23:52 | jrojas92
521 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-05-10 12:23 | 705 |  | 8.6 | 221 | [8 empty] | 0.2 | [13 empty] | ​system good. Reasoning for low free chlorine level is cause the st70 is on the same schedule as tower 1 | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-05-10 12:27 | Daimon A. Boccamazzo
522 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-05-10 12:18 | 894 |  | 8.6 | 216 | [8 empty] | 0.02 | [13 empty] | ​reasoning for free chlorine being so low is the st70 is scheduled for 15 mins Monday through Friday at 10am and I tested at 730 am. Cleaned Chemical loop strainer on tower 1 | Daimon A. Boccamazzo | Not Adjusted |  | 64 | 2016-05-10 12:23 | Daimon A. Boccamazzo
523 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2016-04-27 22:27 | 642 | 791 | 8.5 |  | 220 | 200 |  | 2.42 | 2.1 | 12 | 2.17 | 37 | 0 | 0.092 | 0.28 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​ | jrojas92 |  |  |  | 2016-06-06 22:32 | jrojas92
524 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-27 22:22 | 811 | 114 | 8.4 |  | 170 | 218 |  | 0.82 | 1 | 2 | 0.8 | 0 | 0 | 0.136 | 0.14 | [6 empty] | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 22:27 | jrojas92
525 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-04-21 07:06 | 670 |  | 7.5 | 380 | [8 empty] | 8.8 | [13 empty] | ​free chlorine was off the charts when I tested it. Best conclusion for that is because the st70 and the 3dt222 were set to pump every day for 15 minute intervals once a day and pump speed at over 100, so adjusted the all three pumps. St70 and 3dt222 at 40 and the h550 to 50. Also cleaned out the chemical loop strainer | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-21 07:14 | Daimon A. Boccamazzo
526 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-04-20 07:14 | 760 |  | 8.3 | 308 | [8 empty] | 0 | [13 empty] | ​made adjustments to pump speeds same as the first tower. But the st70 for this tower was on zero so adjusted it to 40. Also cleaned out the chemical loop strainer | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-21 07:19 | Daimon A. Boccamazzo
527 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-04-04 10:55 | 570 | 0 | 8.3 | 310 | [8 empty] | 0 | [13 empty] | ​Tower is running. Controllers are not turned on. Waiting for booster pump to be started​ | Bob A Adams | Not Adjusted |  | 74 | 2016-04-04 10:56 | Bob A Adams
528 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-04-04 10:51 | 359 | 0 | 8.8 | 600 | [8 empty] | 8.4 | [13 empty] | ​​Tower is not running. Controllers are not turned on. Waiting for booster pump to be started. | Bob A Adams | Not Adjusted |  | 57 | 2016-04-04 10:54 | Bob A Adams
529 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2016-03-28 20:27 | 1097 |  | 8.8 |  | 40 | [5 empty] | 1.19 |  | 160 | 0.296 | 1.73 | [11 empty] | ​​Tower was BD for ~15min to reduce high Cl. Tower was off. | jrojas92 |  |  |  | 2016-06-06 20:30 | jrojas92
530 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-28 20:20 | 1112 | 0 | 8.7 |  | 50 | 52 |  | 0.44 | 1.8 | 0 | 1.17 | 0 | 172 | 0.165 | 0.46 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​Tower was BD for ~15min to reduce high Cl. Tower was off for repairs. | jrojas92 |  |  |  | 2016-06-06 20:26 | jrojas92
531 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2015-11-24 14:08 | 655 |  | 8.7 |  | 270 | 280 |  | 8.8 | 0.8 |  | 0.63 | 3 | 0.03 | 0.0882 | 0.16 | [7 empty] | Good | Clean | Clean |  |  | jrojas92 |  |  |  | 2015-12-22 14:10 | jrojas92
532 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 14:04 | 93.2 | 10 | 8.9 |  | 50 | 40 |  | 0.1 | 0.5 | 0 | 0.41 | 0.3 | 0.01 | 0.0319 | 0.08 | [6 empty] | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-12-22 14:07 | jrojas92
533 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-11-16 14:00 | 577 | 4 | 8.7 | 145 | [8 empty] | 0.1 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 62.8 | 2015-11-16 14:03 | Bob A Adams
534 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2015-10-29 15:28 | 572 |  | 8.4 |  | 280 | 238 |  | 3.9 | 0.4 |  | 0.61 | 2 | 0.02 | 0.033 | 0.05 | [12 empty] | jrojas92 |  |  |  | 2015-11-14 15:30 | jrojas92
535 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-29 15:25 | 308 | 130 | 8.1 |  | 90 | 96 |  | 1.11 | 2.5 | 6.8 | 0.56 | 0.7 | 1.07 | 0 | 0.08 | [6 empty] | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 15:28 | jrojas92
536 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2015-10-28 13:57 | 382 |  | 8.5 | 319 | [8 empty] | 6.1 | [13 empty] | ​Trasar meter not calibrated | Bob A Adams | Not Adjusted |  | 78.2 | 2015-11-16 14:00 | Bob A Adams
537 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-10-28 06:39 | 62.8 |  | 8.5 | 145 | [8 empty] | 0.1 | [13 empty] | ​Trasar meter not working. | Bob A Adams | Not Adjusted |  | 62.8 | 2015-11-04 06:41 | Bob A Adams
538 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2015-10-28 06:36 | 382 |  | 8.5 | 319 | [8 empty] | 6.1 | [13 empty] | ​Trasar meter not working. | Bob A Adams | Not Adjusted |  | 78.2 | 2015-11-04 06:39 | Bob A Adams
539 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2015-09-29 19:09 | 637 |  | 8.6 |  | 290 | 298 |  | 3.46 | 0 |  | 0.31 | 0.8 | 0.01 | 0.0346 | 0.11 | [7 empty] | Good |  |  |  |  | jrojas92 |  |  |  | 2015-09-30 19:12 | jrojas92
540 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-29 19:05 | 302 | 144 | 8.2 |  | 120 | 104 |  | 1.17 | 2.6 | 7 | 0.66 | 0.6 | 0 | 0.0566 | 0.13 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​There appears to be water loss from tower through the drain pipe, a small stream. | jrojas92 |  |  |  | 2015-09-30 19:09 | jrojas92
541 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2015-08-26 17:02 | 632 |  | 8.5 |  | 290 | 280 |  | 3.55 | 0.5 |  | 0.41 | 2.9 | 0.04 | 0.0518 | 0.16 | [12 empty] | jrojas92 |  |  |  | 2015-11-14 17:04 | jrojas92
542 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-26 16:59 | 364 | 131 | 8.3 |  | 160 | 138 |  | 1.32 | 3.2 | 4.4 | 0.3 | 0.7 | 0 | 0.0694 | 0.09 | [6 empty] | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 17:02 | jrojas92
543 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-07-16 14:00 | 955 | 33.9 | 8.8 |  | 200 | 294 |  | 0.42 | 0.2 | 0 | 0.22 | 0.4 | 0.03 | 0.0546 | 0.09 | [7 empty] | Good | Clean | Clean | Level Okay | ​There was no flow through the controller. Cooling tower pump was reset and flow started through the controller. | jrojas92 |  |  |  | 2015-08-18 14:06 | jrojas92
544 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2015-06-25 17:53 | 97 |  | 7.9 |  | 50 | 44 |  | 2.06 | 1 |  | 0.52 | 0.9 | 0.03 | 0.0098 | 0.09 | [12 empty] | jrojas92 |  |  |  | 2015-11-14 17:54 | jrojas92
545 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-25 17:49 | 1668 | 64 | 8.4 |  | 430 | 442 |  | 0.75 | 0.7 | 0 | 0.04 | 0.5 | 0.05 | 0.0819 | 0.07 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | There was no flow through controller (high conductivity,etc). | jrojas92 |  |  |  | 2015-11-14 17:53 | jrojas92
546 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-28 18:37 | 836 | 127 | 8.7 |  | 330 | 318 |  | 1.58 | 3.1 | 6.2 | 0.25 | 0.9 | 0.34 | 0.0695 | 0.2 | [12 empty] | jrojas92 |  |  |  | 2015-11-14 18:39 | jrojas92
547 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-19 10:07 | 839.3 |  |  | 249 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-10-01 10:08 | RICHARD A. JOHNSON
548 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:35 | 780 |  |  | 132 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2018-08-30 11:35 | RICHARD A. JOHNSON
549 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 10:31 | 728 |  |  | 215 | [8 empty] | 8.8 | [13 empty] | ​tower fed st70 today. Still need to install the pump for h550. Other than that everything is all good | Daimon A. Boccamazzo | Not Adjusted |  | 83 | 2018-08-10 10:34 | Daimon A. Boccamazzo
550 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 07:04 | 797.2 |  |  | 238 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-07-03 07:05 | RICHARD A. JOHNSON
551 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-25 13:30 | 781.4 |  |  | 308 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-04-30 13:31 | RICHARD A. JOHNSON
552 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-21 10:21 | 736.2 |  |  | 350 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 65 | 2018-02-23 10:22 | RICHARD A. JOHNSON
553 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-29 14:03 | 635 |  |  | 312 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2017-12-29 14:04 | RICHARD A. JOHNSON
554 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-18 10:31 | 657 |  |  | 421 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-10-23 10:34 | RICHARD A. JOHNSON
555 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:13 | 484 |  |  | 157 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2017-08-24 08:14 | RICHARD A. JOHNSON
556 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 07:39 | 504 |  |  | 142 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 80 | 2017-08-02 07:40 | RICHARD A. JOHNSON
557 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-05-02 08:41 | 600 |  | 9.3 | 100 | [8 empty] | 0 | [13 empty] | ​not worried about the low FC levels because the tower is scheduled to feed on Wednesday. | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2017-05-16 08:45 | Daimon A. Boccamazzo
558 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-03 11:51 | 690 |  | 8.7 | 290 | [8 empty] | 8.8 | [13 empty] | ​free chlorine high because the system had fed st70 the day before I had tested it. Changed feeding cycle to 20 mins instead of 30 so the the free chlorine levels aren't to high all the time | Daimon A. Boccamazzo | Not Adjusted |  | 62 | 2017-01-17 11:56 | Daimon A. Boccamazzo
559 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-28 10:59 | 740 |  | 8.5 | 270 | [8 empty] | 8.8 | [13 empty] | ​the free chlorine levels are high because the system had just fed st70 into the tower. Everything else all good | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2016-11-29 11:02 | Daimon A. Boccamazzo
560 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-03 08:50 | 825 |  | 8.9 | 320 | [8 empty] | 8.8 | [13 empty] | ​tower has a high free chlorine level because the system had just pumped st70 into the tower before I tested it | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-10-14 08:52 | Daimon A. Boccamazzo
561 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-02 14:14 | 765 |  | 8.4 | 200 | [8 empty] | 8.8 | [13 empty] | ​​free chlorine levels high because the system had just pumped st70 into the tower and I ended up testing it right after that | Daimon A. Boccamazzo | Not Adjusted |  | 79 | 2016-09-06 14:16 | Daimon A. Boccamazzo
562 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-26 10:16 | 661 |  | 8.6 | 225 | [8 empty] | 8.8 | [13 empty] | ​chenged st70 feeding to 30 mins every mon,wed, and Friday at 8. Instead of feeding for an hour. Seemed like too much for the tower cause my readings were above 8 after 24 hours | Daimon A. Boccamazzo | Not Adjusted |  | 84 | 2016-07-26 10:21 | Daimon A. Boccamazzo
563 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-06 09:09 | 557 |  | 8.6 | 220 | [8 empty] | 8.8 | [13 empty] | ​temperature seems kinda high. Free chlorine off the charts because it just got done feeding for and hour. St70 (Nalco chemical) and ch2o chemicals calls are hooked up but not the 3dt222 and the h-550 | Daimon A. Boccamazzo | Not Adjusted |  | 93 | 2016-06-07 09:13 | Daimon A. Boccamazzo
564 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-23 09:26 | 450 |  | 8.8 | 162 | [8 empty] | 0.1 | [13 empty] | ​controller still won't respond when touching the screen so I wasn't able to check what time the free chlorine gets pumped into the system. Strainer is still good. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-05-23 09:31 | Daimon A. Boccamazzo
565 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 10:22 | 430 |  | 8.65 | 224 | [8 empty] | 0.03 | [13 empty] | ​chemicals are here but not hooked up, still using ch2o unibrom plus. Controller not responding when you push buttons on the screen. Strainer is good | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-05-09 10:27 | Daimon A. Boccamazzo
566 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-18 07:38 | 420 |  | 7.6 | 95 | [8 empty] | 0 | [13 empty] | ​​Nalco controller is hooked up, chemicals are there but it is not operating yet | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-19 07:46 | Daimon A. Boccamazzo
567 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 14:02 | 350 | 0 | 8.1 | 210 | [8 empty] | 0 | [13 empty] | ​Tower is waiting on chem pump, chemicals and controller programming | Bob A Adams | Not Adjusted |  | 77 | 2016-03-31 14:05 | Bob A Adams
568 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-24 09:13 | 784 | 7 | 8.1 | 315 | [8 empty] | 3.1 | [13 empty] | ​posca in range. | Bob A Adams | Not Adjusted |  | 70 | 2016-03-24 09:15 | Bob A Adams
569 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-24 13:53 | 786 | 6 | 8.5 | 280 | [8 empty] | 0.8 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 708 | 2016-02-24 13:56 | Bob A Adams
570 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-11 08:31 | 842 | 8 | 8.5 | 241 | [8 empty] | 1.4 | [13 empty] | Posca in range. Cleaned sensors.​ | Bob A Adams | Not Adjusted |  |  | 2016-02-12 08:33 | Bob A Adams
571 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-09 08:19 | 838 | 8 | 8.4 | 286 | [8 empty] | 2.1 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 69.6 | 2016-02-09 08:21 | Bob A Adams
572 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-26 14:06 | 645 | 6 | 8.5 | 289 | [8 empty] | 1.2 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 70 | 2016-01-28 14:08 | Bob A Adams
573 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-19 14:39 | 564 | 6 | 8.3 | 230 | [8 empty] | 1.8 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 71.3 | 2016-01-19 14:41 | Bob A Adams
574 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-05 10:58 | 636 | 6 | 8.5 | 296 | [8 empty] | 1.6 | [13 empty] | ​cleaned Sensors. Posca in range . Calibrated conductivity and orp | Bob A Adams | Not Adjusted |  | 69.3 | 2016-01-05 11:02 | Bob A Adams
575 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:39 | 649 | 4 | 8.5 | 305 | [8 empty] | 1.2 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 72 | 2015-12-31 07:41 | Bob A Adams
576 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:26 | 615 | 4 | 8.6 | 272 | [8 empty] | 0.6 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 69 | 2015-12-31 07:31 | Bob A Adams
577 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 06:44 | 633 | 4 | 8.5 | 310 | [8 empty] | 1.3 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 73.5 | 2015-12-09 06:46 | Bob A Adams
578 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-19 14:06 | 641 | 4 | 8.6 | 286 | [8 empty] | 0.8 | [13 empty] | ​cleaned sensors and Posca in range | Bob A Adams | Not Adjusted |  | 72 | 2015-11-30 14:08 | Bob A Adams
579 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-09 14:00 | 632 | 6 | 8.6 | 255 | [8 empty] | 0.6 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 69 | 2015-11-30 14:06 | Bob A Adams
580 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-28 06:52 | 586 | 6 | 8.5 | 279 | [8 empty] | 0.8 | [14 empty] | Bob A Adams | Not Adjusted |  | 73.3 | 2015-11-03 06:54 | Bob A Adams
581 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-27 14:29 | 589 | 6 | 8.5 | 248 | [8 empty] | 0.5 | [13 empty] | ​Posca and conductivity in range | Bob A Adams | Not Adjusted |  | 72 | 2015-10-28 14:33 | Bob A Adams
582 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-05 14:27 | 612 | 6 | 8.5 | 300 | [8 empty] | 1.6 | [13 empty] | ​Posca in range. Cleaned sensors. | Bob A Adams | Not Adjusted |  | 75 | 2015-10-05 14:29 | Bob A Adams
583 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-05 06:47 | 571 | 6 | 8.5 | 67 | [8 empty] | 0 | [13 empty] | ​Bromine pump failed and was replaced. Cleaned sensors. Posca is in range. | Bob A Adams | Not Adjusted |  | 73 | 2015-10-08 06:51 | Bob A Adams
584 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-23 06:27 | 640 | 8 | 8.5 | [9 empty] | 0.6 | [13 empty] | ​posca is in range. ORP is 261 | Bob A Adams | Not Adjusted |  | 78 | 2015-09-23 06:30 | Bob A Adams
585 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-25 09:01 | 631 |  | 8.5 | [23 empty] | ​ORP = 252 TWO = 0.6 OP = 6 | mrh4 | Not Adjusted |  | 76 | 2015-09-23 09:02 | Marilyn Fick
586 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-18 09:00 | 631 |  | 8.5 | [23 empty] | ​ORP = 221 TWO = 0.2​ OP = 6 | mrh4 | Not Adjusted |  | 80 | 2015-09-23 09:01 | Marilyn Fick
587 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-11 08:59 | 635 |  | 8.5 | [23 empty] | ​ORP = 247​ TWO = 0.7 OP = 6 | mrh4 | Not Adjusted |  | 75.4 | 2015-09-23 09:00 | Marilyn Fick
588 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-04 08:58 | 656 |  | 8.4 | [23 empty] | ORP = 260 TWO = 2.4 OP = 4​ | mrh4 | Not Adjusted |  | 76.3 | 2015-09-23 08:59 | Marilyn Fick
589 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-01 08:57 | 639 |  | 8.5 | [23 empty] | ​ORP = 268 TWO = 1.5 OP = 4 POSCA 260-275 | mrh4 | Not Adjusted |  | 79.2 | 2015-09-23 08:58 | Marilyn Fick
590 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-05 08:55 | 601 |  | 8.4 | [23 empty] | ​ORP = 279 TWO = 0.8 OP = 6 | mrh4 | Not Adjusted |  | 74.2 | 2015-09-23 08:57 | Marilyn Fick
591 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-01 08:53 | 631 |  | 8.4 | [23 empty] | ​ORP = 301 TWO = 2 OP = 2 POSCA ON 10 MIN | mrh4 | Not Adjusted |  | 73.9 | 2015-09-23 08:55 | Marilyn Fick
592 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-20 08:52 | 618 |  | 8.4 | [23 empty] | ​ORP = 246​ TWO = 0.7 OP = 6 | mrh4 | Not Adjusted |  | 76 | 2015-09-23 08:53 | Marilyn Fick
593 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-20 08:44 | 618 |  | 8.4 | [23 empty] | ​ ORP - 246 TWO - .7 OP - 6 | mrh4 | Not Adjusted |  | 76 | 2015-09-21 08:52 | Jay Dahlstrom
594 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-01 08:49 | 608 |  | 8.4 | [23 empty] | ​ORP = 274 TWO = 0.5 OP = 4 | mrh4 | Not Adjusted |  | 72 | 2015-09-23 08:52 | Marilyn Fick
595 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-23 08:47 | 619 |  | 8.5 | [23 empty] | ​ORP = 272 TWO = 0.1 OP = 2 | mrh4 | Not Adjusted |  | 70.2 | 2015-09-23 08:48 | Marilyn Fick
596 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 08:45 | 622 |  | 8.5 | [23 empty] | ​ORP = 278 TWO = 0.2 OP = 6​ POSCA 250-260 ppm | mrh4 | Not Adjusted |  | 70.2 | 2015-09-23 08:47 | Marilyn Fick
597 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 08:43 | 606 |  | 8.4 | [23 empty] | ​​ORP = 274 TWO = 0.8 OP = 4 Turned on POSCA 10 | mrh4 | Not Adjusted |  | 71.5 | 2015-09-23 08:45 | Marilyn Fick
598 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-16 13:53 | 590 |  | 7.7 | [23 empty] | ​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.7 | 2015-09-21 13:53 | Jay Dahlstrom
599 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-09 08:42 | 608 |  | 8.3 | [23 empty] | ​ORP = 272 TWO = 0.6 OP = 6 | mrh4 | Not Adjusted |  | 72 | 2015-09-23 08:43 | Marilyn Fick
600 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-27 08:41 | 608 |  | 8.3 | [23 empty] | ​ORP = 280 TWO = 0.9 OP = 6 POSCA 240-250 | mrh4 | Not Adjusted |  | 72 | 2015-09-23 08:42 | Marilyn Fick
601 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-13 08:35 | 727 |  | 8.4 | [23 empty] | ​ORP = 273 TWO = 0.6 OP = 6​ POSCA 230 - 240 pms | mrh4 | Not Adjusted |  | 71.7 | 2015-09-23 08:36 | Marilyn Fick
602 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-04 08:33 | 613 |  | 8.1 | [23 empty] | ​​ORP = 158 TWO = 0 OP = 4 | mrh4 | Not Adjusted |  | 67.9 | 2015-09-23 08:34 | Marilyn Fick
603 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-03 08:32 | 639 |  | 8.1 | [23 empty] | ​ORP = 199 TWO = 0.3 OP = 6 | mrh4 | Not Adjusted |  | 70.5 | 2015-09-23 08:33 | Marilyn Fick
604 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-26 08:31 | 595 |  | 8.3 | [23 empty] | ​ORP = 200 TWO = ​0.1 OP = 8 | mrh4 | Not Adjusted |  | 67.5 | 2015-09-23 08:32 | Marilyn Fick
605 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-18 08:28 | 533 |  | 8.4 | [23 empty] | ​​ORP = 240 TWO = 0.8 OP = 8 | mrh4 | Not Adjusted |  | 68.4 | 2015-09-23 08:29 | Marilyn Fick
606 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-05 08:26 | 632 |  | 7.8 | [23 empty] | ​​​​ORP = 245 TWO = 0.9 OP = 4 | mrh4 | Not Adjusted |  | 71.7 | 2015-09-23 08:28 | Marilyn Fick
607 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-27 08:24 | 564 |  | 8.5 | [23 empty] | ORP = 245 TWO = 1.0 OP = 6 | mrh4 | Not Adjusted |  | 71.1 | 2015-09-23 08:26 | Marilyn Fick
608 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-22 08:23 | 648 |  | 8.4 | [23 empty] | ​ORP = 240 TWO = 0.6​ OP = 4 | mrh4 | Not Adjusted |  | 70.5 | 2015-09-23 08:24 | Marilyn Fick
609 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-15 08:21 | 596 |  | 8.2 | [23 empty] | ​​ORP = 268 TWO = 1.1 OP = 6 | mrh4 | Not Adjusted |  | 68.8 | 2015-09-23 08:22 | Marilyn Fick
610 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-05 08:11 | 606 |  | 8.2 | [23 empty] | TWO = 1.0​ OP = 6 | mrh4 | Not Adjusted |  | 72.3 | 2015-09-23 08:20 | Marilyn Fick
611 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-20 10:10 | 1519 |  |  | 282 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-10-01 10:10 | RICHARD A. JOHNSON
612 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:36 | 1953 |  |  | 142 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 66 | 2018-08-30 11:36 | RICHARD A. JOHNSON
613 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 10:43 | 694 |  |  | 254 | [8 empty] | 0.4 | [13 empty] | ​system still pretty dirty but good flow going through the loop. Tower will feed st70 later today so FC levels are okay for now. Cleaned strainer and conductivity probe. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2018-08-10 10:46 | Daimon A. Boccamazzo
614 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 07:02 | 645 |  |  | 197 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-07-03 07:03 | RICHARD A. JOHNSON
615 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-22 10:16 | 962.3 |  |  | 255 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2018-02-23 10:17 | RICHARD A. JOHNSON
616 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-28 14:00 | 311 |  |  | 192 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 65 | 2017-12-29 14:00 | RICHARD A. JOHNSON
617 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-19 10:27 | 316 |  |  | 203 | [8 empty] | 0.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2017-10-23 10:29 | RICHARD A. JOHNSON
618 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:22 | 1355 |  |  | 168 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2017-08-24 08:22 | RICHARD A. JOHNSON
619 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 07:44 | 349 |  |  | 160 | [8 empty] | 0.4 | [13 empty] | ​tested on a feed day | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2017-08-02 07:46 | RICHARD A. JOHNSON
620 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-03 12:12 | 3370 |  | 8.6 | 307 | [8 empty] | 1.1 | [13 empty] | ​​drained water out of the system so that make up water would go into the system and bring the conductivity down to at least 1800. Also cleaned the strainer, flow meter, and conductivity sensor. | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2017-01-17 12:18 | Daimon A. Boccamazzo
621 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-28 11:07 | 3366 |  | 8.5 | [9 empty] | 0.2 | [13 empty] | ​cond was way too high so I drained water so that fresh water would fill the system | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2016-11-29 11:15 | Daimon A. Boccamazzo
622 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-03 08:57 | 2800 |  | 9 | 281 | [8 empty] | 2.6 | [13 empty] | ​drained water out of the system to bring fresh water in so the conductivity would go down. I think the conductivity sensor needs to be calibrated cause it is reading 1700 and my meter read 2800. I cleaned the flow and conductivity sensor and also the strainer. | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-10-14 09:01 | Daimon A. Boccamazzo
623 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-02 14:23 | 3368 |  | 8.6 | 300 | [8 empty] | 0.2 | [13 empty] | ​​drained water of the system so I could get some fresh water in the tower and bring the conductivity down. I cleaned the strainer, flow, and conductivity sensors. Also I pumped st70 into the system for 45 mins | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-09-06 14:26 | Daimon A. Boccamazzo
624 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-26 10:25 | 1747 |  | 8.7 | 248 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Tower feeds st70 tomorrow so the free chlorine levels should be up then. | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-07-26 10:28 | Daimon A. Boccamazzo
625 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-28 13:47 | 378 |  | 8.5 | 133 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer, flow sensor, and conductivity sensor. Changed st70 timer to mon, wed, and fri for an hour at 11am and put a timer for h-550 for 15 minutes at 9am mon-fri. Conductivity sensor needs to be calibrated, it is reading 1100 and my meter is reading 378 | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-06-28 13:56 | Daimon A. Boccamazzo
626 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-23 11:10 | 2122 |  | 8.9 | 244 | [8 empty] | 0.5 | [13 empty] | ​cleaned strainer. Need reminding on how to force bleed the tower without the controller so I can bring the conductivity down. Need update on getting this controller on and running. I don't know how to force st70 into the system without the controller being on. | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-05-23 11:14 | Daimon A. Boccamazzo
627 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 08:58 | 1275 | [25 empty] | ​forced bled the tower water and forced some make up water in the system to bring the conductivity down which was 2300 when I first got there | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-12 08:59 | Daimon A. Boccamazzo
628 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 12:07 | 2244 |  | 8.89 | 232 | [8 empty] | 0.06 | [13 empty] | ​chemical loop strainer was really dirty, I cleaned it but it will need to be cleaned again in a couple of days. There was a leak on the 3dt222 porta feed cause there were fittings that were loose but they got tightened and the leak is no more | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-05-10 12:11 | Daimon A. Boccamazzo
629 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-19 09:16 | 1385 |  | 8.2 | 124 | [8 empty] | 0.1 | [13 empty] | ​Nalco controller was not on, portal feeds are there but there is no chemicals in them, cleaned piping strainer. Also drained water to bring the conductivity down and opened the make up water valve to make sure that was enough water in the tower | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-19 09:21 | Daimon A. Boccamazzo
630 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-04 11:00 | 352 | 0 | 8.4 | 190 | [8 empty] | 0 | [13 empty] | ​Added Posca and Bromine to sump | Bob A Adams | Not Adjusted |  | 60 | 2016-04-04 11:02 | Bob A Adams
631 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-01 13:38 | 894 | 0 | 8.6 | 194 | [8 empty] | 0.1 | [13 empty] | ​Nalco is in progress of installing new system. Tanks in place waiting for chemical and pumps | Bob A Adams | Not Adjusted |  | 54 | 2016-04-01 13:40 | Bob A Adams
632 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-24 10:58 | 642 | 8 | 8.4 | 238 | [8 empty] | 0.1 | [13 empty] | ​posca in range. Bromine was empty, replaced | Bob A Adams | Not Adjusted |  | 51.7 | 2016-03-24 11:02 | Bob A Adams
633 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-07 07:21 | 642 | 8 | 8.1 | 406 | [8 empty] | 1.1 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 50.1 | 2016-03-07 07:24 | Bob A Adams
634 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-09 14:40 | 654 | 8 | 8.5 | 286 | [8 empty] | 1.8 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 67.2 | 2016-02-09 14:42 | Bob A Adams
635 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-26 14:08 | 652 | 7 | 8.4 | 360 | [8 empty] | 2 | [14 empty] | Bob A Adams | Not Adjusted |  | 69.2 | 2016-01-28 14:10 | Bob A Adams
636 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-15 08:54 | 644 | 8 | 8.5 | 267 | [8 empty] | 0.8 | [13 empty] | ​Posca in range. | Bob A Adams | Not Adjusted |  | 68 | 2016-01-15 08:56 | Bob A Adams
637 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-11 06:28 | 653 | 11 | 8.5 | 170 | [8 empty] | 0.1 | [13 empty] | ​Posca in range. Cleaned sensors. | Bob A Adams | Not Adjusted |  | 67 | 2016-01-12 06:35 | Bob A Adams
638 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-05 07:08 | 640 | 12 | 8.4 | 310 | [8 empty] | 1.2 | [13 empty] | ​Posca in range. Cleaned sensors. Calibrated orp. | Bob A Adams | Not Adjusted |  | 68.1 | 2016-01-05 07:11 | Bob A Adams
639 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:31 | 642 | 6 | 8.5 | 252 | [8 empty] | 0.8 | [14 empty] | Bob A Adams | Not Adjusted |  | 70.1 | 2015-12-31 07:34 | Bob A Adams
640 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 06:50 | 653 | 6 | 8.6 | 256 | [8 empty] | 0.7 | [13 empty] | ​cleaned sensors. Posca in range. | Bob A Adams | Not Adjusted |  | 69.1 | 2015-12-09 06:53 | Bob A Adams
641 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-07 06:37 | 643 | 4 | 8.5 | 310 | [8 empty] | 1.2 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 70 | 2015-12-09 06:40 | Bob A Adams
642 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-03 14:32 | 636 | 6 | 8.5 | 320 | [8 empty] | 1.3 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 69 | 2015-12-04 14:34 | Bob A Adams
643 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-30 13:51 | 651 | 6 | 8.6 | 141 | [8 empty] | 0.2 | [13 empty] | ​Posca in range. Chlorine in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 68.9 | 2015-11-30 13:53 | Bob A Adams
644 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-12 13:51 | 650 | 6 | 8.5 | 228 | [8 empty] | 0.1 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 69.3 | 2015-11-16 13:53 | Bob A Adams
645 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-06 14:00 | 648 | 10 | 8.5 | 197 | [8 empty] | 0.1 | [13 empty] | ​​Posca in range. Cleaned sensors. Set time | Bob A Adams | Not Adjusted |  | 70.7 | 2015-11-06 14:03 | Bob A Adams
646 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-27 14:21 | 626 | 8 | 8.5 | 281 | [8 empty] | 0.7 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 68 | 2015-10-28 14:23 | Bob A Adams
647 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-06 06:42 | 648 | 8 | 8.6 | 275 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Cleaned sensors. | Bob A Adams | Not Adjusted |  | 68.5 | 2015-10-08 06:46 | Bob A Adams
648 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-28 14:03 | 649 | 6 | 8.5 | 268 | [8 empty] | 0.5 | [14 empty] | Bob A Adams | Not Adjusted |  | 68.5 | 2015-10-01 14:05 | Bob A Adams
649 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-24 13:16 | 637 |  | 8.5 | [23 empty] | ​​ORP= 280 TWO= .5 OP= 6 | mrh4 | Not Adjusted |  | 66.3 | 2015-09-24 13:17 | Cesar Escobar
650 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-24 13:12 | 654 |  | 8.2 | [23 empty] | ​​ORP= 258 TWO= .8 OP= 6 | mrh4 | Not Adjusted |  | 68 | 2015-09-24 13:13 | Cesar Escobar
651 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-21 07:04 | 667 | 4 | 8.3 | [9 empty] | 0.3 | [13 empty] | ​posca was in range. 283 orp | Bob A Adams | Not Adjusted |  | 68.3 | 2015-09-21 07:11 | Bob A Adams
652 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-20 13:31 | 647 |  | 8.5 | [23 empty] | ​​ORP= 301 TWO= 1.1 OP= 6 | mrh4 | Not Adjusted |  | 67 | 2015-09-24 13:32 | Cesar Escobar
653 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-10 13:29 | 643 |  | 8.5 | [23 empty] | ​​ORP= 279 TWO= .7 OP= 6 | mrh4 | Not Adjusted |  | 69.5 | 2015-09-24 13:31 | Cesar Escobar
654 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-05 13:28 | 641 |  | 8.7 | [23 empty] | ​​ORP= 200 TWO= .1 OP= 8 | mrh4 | Not Adjusted |  | 69.1 | 2015-09-24 13:29 | Cesar Escobar
655 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-03 13:27 | 648 |  | 8.5 | [23 empty] | ​​ORP= 269 TWO= 1.0 OP= 6 | mrh4 | Not Adjusted |  | 69 | 2015-09-24 13:28 | Cesar Escobar
656 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-02 13:26 | 651 |  | 8.5 | [23 empty] | ​​ORP= 262 TWO= .9 OP= 6 | mrh4 | Not Adjusted |  | 68 | 2015-09-24 13:27 | Cesar Escobar
657 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-12 13:24 | 635 |  | 8.5 | [23 empty] | ​ORP= 292 TWO= .9 OP= 8 | mrh4 | Not Adjusted |  | 68.2 | 2015-09-24 13:26 | Cesar Escobar
658 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-08 13:23 | 645 |  | 8.5 | [23 empty] | ​ORP= 313 TWO= 1.8 OP= 6 | mrh4 | Not Adjusted |  | 69.1 | 2015-09-24 13:24 | Cesar Escobar
659 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-29 13:22 | 646 |  | 8.5 | [23 empty] | ​​ORP= 305 TWO= 1.5 OP= 8 | mrh4 | Not Adjusted |  | 69 | 2015-09-24 13:23 | Cesar Escobar
660 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-24 13:21 | 644 |  | 8.4 | [23 empty] | ​​ORP= 281 TWO= .8 OP= 8 | mrh4 | Not Adjusted |  | 68.1 | 2015-09-24 13:22 | Cesar Escobar
661 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-23 13:20 | 648 |  | 8.6 | [23 empty] | ​ORP= 305 TWO= 1.7 OP= 6 | mrh4 | Not Adjusted |  | 68.9 | 2015-09-24 13:21 | Cesar Escobar
662 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 13:19 | 630 |  | 8.5 | [23 empty] | ​​ORP= 320 TWO= 1.3 OP= 4 | mrh4 | Not Adjusted |  | 68.8 | 2015-09-24 13:20 | Cesar Escobar
663 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 13:17 | 637 | [25 empty] | ​​ORP= 124 TWO= 0 OP= 6 | mrh4 | Not Adjusted |  | 68.4 | 2015-09-24 13:19 | Cesar Escobar
664 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-30 13:14 | 666 |  | 8.4 | [23 empty] | ​​ORP= 400 TWO= 1.4 OP= 4 POSCA 13-16 PMS | mrh4 | Not Adjusted |  | 68 | 2015-09-24 13:16 | Cesar Escobar
665 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-19 13:13 | 642 |  | 8.5 | [23 empty] | ​​ORP= 132 TWO= 0 OP= 6 | mrh4 | Not Adjusted |  | 67.9 | 2015-09-24 13:14 | Cesar Escobar
666 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-12 13:09 | 642 |  | 8.5 | [23 empty] | ​​ORP= 260 TWO= .1 OP= 6 | mrh4 | Not Adjusted |  | 70.1 | 2015-09-24 13:11 | Cesar Escobar
667 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-04 13:11 | 707 |  | 8.5 | [23 empty] | ​ORP= 168 TWO= 0 OP= 6 | mrh4 | Not Adjusted |  | 66.8 | 2015-09-24 13:12 | Cesar Escobar
668 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-26 08:39 | 649 |  | 8.6 | [23 empty] | ​​ORP= 264 TWO= .2 OP= 8 | mrh4 | Not Adjusted |  | 69 | 2015-09-24 08:40 | Cesar Escobar
669 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-20 08:38 | 642 |  | 8.6 | [23 empty] | ​​ORP= 252 TWO= .1 OP= 8 | mrh4 | Not Adjusted |  | 68.3 | 2015-09-24 08:39 | Cesar Escobar
670 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-18 08:36 | 59.6 |  | 8.6 | [23 empty] | ​​ORP= 350 TWO= 1.3 OP= 10 | mrh4 | Not Adjusted |  | 66.5 | 2015-09-24 08:38 | Cesar Escobar
671 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-10 08:35 | 645 |  | 8.6 | [23 empty] | ​​ORP= 254 TWO= .5 OP= 6 | mrh4 | Not Adjusted |  | 69.2 | 2015-09-24 08:36 | Cesar Escobar
672 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-06 08:34 | 650 |  | 8.5 | [23 empty] | ​​ORP= 170 TWO= .1 OP= 10 | mrh4 | Not Adjusted |  | 68.7 | 2015-09-24 08:35 | Cesar Escobar
673 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-28 08:32 | 647 |  | 8.6 | [23 empty] | ​​ORP= 245 TWO= .6 OP= 4 | mrh4 | Not Adjusted |  | 68.9 | 2015-09-24 08:34 | Cesar Escobar
674 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-23 08:31 | 649 |  | 8.6 | [23 empty] | ​OP= 8 | mrh4 | Not Adjusted |  | 68.5 | 2015-09-24 08:32 | Cesar Escobar
675 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-16 08:22 | 625 |  | 8.6 | [23 empty] | ​ORP= 270 TWO= .5 OP= 8 | mrh4 | Not Adjusted |  | 67.6 | 2015-09-24 08:26 | Cesar Escobar
676 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 10:24 | [26 empty] | ​tower still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2018-08-10 10:25 | Daimon A. Boccamazzo
677 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2017-09-13 13:59 | [26 empty] | ​tower is still offline. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-09-13 14:01 | Daimon A. Boccamazzo
678 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2017-05-02 08:38 | [26 empty] | ​tower is still offline. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-05-16 08:40 | Daimon A. Boccamazzo
679 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-03 11:49 | [26 empty] | ​still the same as last time I checked | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-17 11:50 | Daimon A. Boccamazzo
680 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-28 10:57 | [26 empty] | ​still offline but ready to be put back online | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-11-29 10:58 | Daimon A. Boccamazzo
681 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-03 08:46 | [26 empty] | ​​tower is still offline still but it is ready to go back online. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-10-14 08:49 | Daimon A. Boccamazzo
682 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-26 10:12 | [26 empty] | Tower is still offline. New walchem controller put in and new chemicals all reading to go when tower starts up | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-07-26 10:15 | Daimon A. Boccamazzo
683 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-06 09:06 | [26 empty] | ​old chemicals still hooked up. Cooling tower still offline for repairs, no new progress made that I could see sense the last time I was there. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-06-07 09:08 | Daimon A. Boccamazzo
684 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-23 09:22 | [26 empty] | ​tower is still offline. Looks the same as last time I checked it | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-23 09:24 | Daimon A. Boccamazzo
685 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 10:19 | [26 empty] | ​cooling tower still offline. Plumbers getting further on repairs | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-09 10:21 | Daimon A. Boccamazzo
686 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-18 11:28 | 420 |  | 7.6 | 95 | [8 empty] | 0 | [13 empty] | ​Nalco controller is hooked up, Chemicals are there but it is not operating yet WRONG TOWER THIS IS RR-WING--DN3 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-18 11:31 | Daimon A. Boccamazzo
687 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-18 10:23 | [26 empty] | ​tower is off for repairs | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-18 10:23 | Daimon A. Boccamazzo
688 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 13:59 | 0 | 0 | 0 | 0 | [8 empty] | 0 | [13 empty] | ​Tower is empty, power off, water off | Bob A Adams | Not Adjusted |  | 0 | 2016-03-31 14:01 | Bob A Adams
689 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-24 09:11 | 0 | 0 | 0 | 0 | [8 empty] | 0 | [13 empty] | ​cooling tower fan and water turned off. Drain open | Bob A Adams | Not Adjusted |  | 0 | 2016-03-24 09:12 | Bob A Adams
690 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 10:47 | [26 empty] | ​tower still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2018-03-16 10:48 | Daimon A. Boccamazzo
691 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 11:14 | [26 empty] | ​tower is offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-09-11 11:16 | Daimon A. Boccamazzo
692 | 1197 | 1197-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-03-17 13:36 | 500 | 200 | 7.6 | [9 empty] | 2 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​​Blowdown solenoid not closing. May have debris caught in it. I recommend cleaning or replacing. | reedhea |  |  |  | 2017-03-17 13:38 | reedhea
693 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-20 07:19 | [26 empty] | ​tower is still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-26 07:22 | Daimon A. Boccamazzo
694 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-05 07:52 | [26 empty] | ​still same as I left it last time | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-12-07 07:54 | Daimon A. Boccamazzo
695 | 1197 | 1197-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 12:42 | [26 empty] | ​System not running | reedhea |  |  |  | 2016-11-09 13:42 | reedhea
696 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-18 13:58 | [26 empty] | ​tower still offline until further notice | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-10-24 14:01 | Daimon A. Boccamazzo
697 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-18 12:16 | [26 empty] | ​tower still offline. Chemicals there and new transatlantic controller there and ready to go | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-07-19 12:17 | Daimon A. Boccamazzo
698 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:19 | [26 empty] | ​tower is still off line. New Nalco controller is set up and ready to go, there is also chemicals ready to be hooked up. Just waiting to get the tower fixed and turned on | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-06-02 13:21 | Daimon A. Boccamazzo
699 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-16 13:16 | [26 empty] | ​tower is still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-16 13:17 | Daimon A. Boccamazzo
700 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-08 14:13 | 0 | 0 | 0 | 0 | [8 empty] | 0 | [13 empty] | ​​tower is turned off drained | Bob A Adams | Not Adjusted |  | 0 | 2016-04-08 14:14 | Bob A Adams
701 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 11:02 | 0 | 0 | 0 | 0 | [8 empty] | 0 | [13 empty] | ​Water and power are turned off at tower. Tower is drained and drain is open. | Bob A Adams | Not Adjusted |  | 0 | 2016-04-04 11:05 | Bob A Adams
702 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-14 10:25 | 928.2 |  |  | 131 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-10-01 10:26 | RICHARD A. JOHNSON
703 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-25 09:25 | 837.2 |  |  | 166 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-07-30 09:26 | RICHARD A. JOHNSON
704 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-21 10:32 | 1886 |  |  | 227 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2018-05-31 10:33 | RICHARD A. JOHNSON
705 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-22 07:51 | 847 |  |  | 160 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-04-02 07:52 | RICHARD A. JOHNSON
706 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 08:40 | 1000 |  |  | 200 | [8 empty] | 0.2 | [13 empty] | ​levels are okay. St70 scheduled to feed later today | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2018-03-16 08:51 | Daimon A. Boccamazzo
707 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-21 12:05 | 1122 |  |  | 163 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 64 | 2017-12-04 12:07 | RICHARD A. JOHNSON
708 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 10:37 | 579 |  |  | 204 | [8 empty] | 0.2 | [13 empty] | ​nothing too alarming, needs st70 jug | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2017-09-11 10:48 | Daimon A. Boccamazzo
709 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:18 | 613 |  |  | 241 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-02 10:19 | RICHARD A. JOHNSON
710 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:26 | 603 |  | 8.6 | 305 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-06-19 07:28 | RICHARD A. JOHNSON
711 | 1150 | 1150-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-10 12:17 | 611 | 101 | 8.2 |  | 70 | 100 | [6 empty] | 0 |  |  |  | 8790.95 |  |  |  |  | Correct | Good | Dirty | Clean | Needs Filling | ​I cleaned out the basket strainer and replaced the ST70 chemical pail. The H550 needs to be replaced. Note: Meter reading is in gallons. | reedhea |  |  |  | 2017-05-10 12:18 | reedhea
712 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-19 13:36 | 551 |  | 9 | 264 | [8 empty] | 0.3 | [13 empty] | ​fixed chemical pumps that were leaking before. And fed st70 for 30 mins to bring the chlorine levels up | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2017-01-25 13:40 | Daimon A. Boccamazzo
713 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-09 13:06 | 2148 |  | 7.9 | 90 | [8 empty] | 0.1 | [13 empty] | ​drained some water out of the system to bring conductivity down. Cleaned strainer, flow and conductivity sensors and opened up two valves connected to a pump that tied into the chemical loop | Daimon A. Boccamazzo | Not Adjusted |  | 63 | 2016-09-12 13:10 | Daimon A. Boccamazzo
714 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-01 14:53 | 690 |  | 8 | 182 | [8 empty] | 0.1 | [13 empty] | ​new Nalco controller but still using ch2o chemical. Need to order Nalco chemicals jugs for the system and hook them up. Tower is good. Strainer will need to be cleaned next time around. | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-06-01 14:55 | Daimon A. Boccamazzo
715 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-13 07:24 | 681 |  | 8.7 | 242 | [8 empty] | 1.2 | [13 empty] | ​new Nalco controller hooked up. Chemicals are not here yet, strainer is okay | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2016-05-16 07:27 | Daimon A. Boccamazzo
716 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 13:08 | 715 |  | 8.6 | 410 | [8 empty] | 8.8 | [13 empty] | ​old walchem controllers, don't know how to use it to check it and see when the system pumped st70 into it. Still good amount of chemical in the buckets. Also controllers said normal on both of them. | Daimon A. Boccamazzo | Not Adjusted |  | 63 | 2016-04-29 13:12 | Daimon A. Boccamazzo
717 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-07 14:23 | 750 | 6 | 8.3 | 285 | [8 empty] | 0.5 | [13 empty] | Posca in range ​ | Bob A Adams | Not Adjusted |  | 66 | 2016-04-07 14:27 | Bob A Adams
718 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 06:35 | 745 | 9 | 8.4 | 213 | [8 empty] | 0.5 | [13 empty] | Posca in range ​ | Bob A Adams | Not Adjusted |  | 63 | 2016-03-29 06:37 | Bob A Adams
719 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-11 14:04 | 455 | 4 | 8.5 | 262 | [8 empty] | 0.4 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 63 | 2016-03-11 14:06 | Bob A Adams
720 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-22 14:14 | 487 | 6 | 8.4 | 253 | [8 empty] | 0.5 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 64 | 2016-02-22 14:16 | Bob A Adams
721 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 11:19 | 558 | 6 | 8.4 | 293 | [8 empty] | 0.4 | [13 empty] | ​free chlorine in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 67 | 2016-02-08 11:22 | Bob A Adams
722 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-28 14:19 | 610 | 8 | 8.5 | 252 | [8 empty] | 0.6 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 64 | 2016-01-28 14:21 | Bob A Adams
723 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-14 10:46 | 918 | 10 | 8.6 | 267 | [8 empty] | 0.2 | [13 empty] | ​Posca and free chlorine in range. Cleaned sensors. Calibrated conductivity and orp. Conductivity sensor failed. Replaced conductivity sensor. | Bob A Adams | Not Adjusted |  | 68 | 2016-01-14 10:49 | Bob A Adams
724 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 13:02 | 760 | 12 | 8.6 | 164 | [8 empty] | 0 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 63 | 2015-12-31 13:05 | Bob A Adams
725 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 09:55 | 621 | 8 | 8.1 | 221 | [8 empty] | 0 | [13 empty] | ​CH20 treatment system Primed bromine pump | mrh4 | Not Adjusted |  | 71 | 2015-12-14 09:58 | mrh4
726 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-09 11:28 | 567 | 8 | 8 | 210 | [8 empty] | 0 | [14 empty] | mrh4 | Not Adjusted |  | 66.3 | 2015-11-24 11:30 | mrh4
727 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-04 14:47 | 551 | 8 | 8.1 | 221 | [8 empty] | 0 | [13 empty] | ​CH20 system Primed bromine pump | mrh4 | Not Adjusted |  | 67.1 | 2015-11-04 14:51 | mrh4
728 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-04 08:57 | 551 | 8 | 8 | 221 | [8 empty] | 0 | [13 empty] | ​CH20 tower Primed bromine pump | mrh4 | Not Adjusted |  | 67.1 | 2015-11-23 09:04 | mrh4
729 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-23 09:44 | 614 | 8 | 8.1 | 221 | [8 empty] | 4 | [13 empty] | ​CH20 system. Test results are within their parameters Reduced bromine pump speed | mrh4 | Not Adjusted |  | 71.1 | 2015-10-26 09:49 | mrh4
730 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-01 14:03 | 352 | 8 | 8.1 | [9 empty] | 0 | [13 empty] | ​ ​Ch2O System C/T has slow leak in drain line. Due to a possible clogged drain C/T drains to parking lot | mrh4 | Up |  |  | 2015-10-01 14:09 | mrh4
731 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-22 14:52 | 426 | 8 | 7.85 | [9 empty] | 0 | [13 empty] | ​This is a Ch2O system and is within recommended parameters except for FC Bromine pump needed to be primed and is now at 3 ppm | mrh4 | Not Adjusted |  |  | 2015-09-22 14:57 | mrh4
732 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 13:58 | 591 |  | 8.1 | [23 empty] | ​​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.9 | 2015-09-21 13:58 | Jay Dahlstrom
733 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-13 13:34 | 607 |  | 8 | [23 empty] | TEI - 3 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 18.4 | 2015-09-21 13:34 | Jay Dahlstrom
734 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-06 13:00 | 654 |  | 7.9 | [23 empty] | ​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 18.1 | 2015-09-21 13:01 | Jay Dahlstrom
735 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-02 12:56 | 606 |  | 8 | [23 empty] | TEI - 4 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 18.1 | 2015-09-21 12:56 | Jay Dahlstrom
736 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-19 12:48 | 589 |  | 8.1 | [23 empty] | ​TEI - 8 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.5 | 2015-09-21 12:49 | Jay Dahlstrom
737 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-03 10:17 | 584 |  | 8.1 | [23 empty] | ​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 16.6 | 2015-09-21 10:18 | Jay Dahlstrom
738 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-25 10:10 | 624 |  | 8.1 | [23 empty] | ​TEI - 4 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 22.1 | 2015-09-21 10:11 | Jay Dahlstrom
739 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-20 09:20 | 597 |  | 8 | [23 empty] | ​​TEI - 6 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.1 | 2015-09-21 09:21 | Jay Dahlstrom
740 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-10 09:11 | 617 |  | 8.7 | [23 empty] | ​​TEI - 8 ppm POSCA - 6 ppm | mrh4 | Not Adjusted |  | 19.4 | 2015-09-21 09:12 | Jay Dahlstrom
741 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-14 10:26 | 755 |  |  | 154 | [8 empty] | 2.7 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-10-01 10:27 | RICHARD A. JOHNSON
742 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-26 09:28 | 752.7 |  |  | 163 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 79 | 2018-07-30 09:29 | RICHARD A. JOHNSON
743 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-21 10:31 | 767.3 |  |  | 263 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-05-31 10:31 | RICHARD A. JOHNSON
744 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 08:35 | 690 |  |  | 245 | [8 empty] | 0.3 | [13 empty] | ​manually fed st70 into the system for 30mins to bring the FC levels up. No flow in system cause tower is on winter mode | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2018-03-16 08:37 | Daimon A. Boccamazzo
745 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-30 13:19 | 662 |  |  | 181 | [8 empty] | 0.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-02-01 13:20 | RICHARD A. JOHNSON
746 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-21 12:04 | 750 |  |  | 197 | [8 empty] | 0.2 | [13 empty] | ​ | RICHARD A. JOHNSON | Not Adjusted |  | 63 | 2017-12-04 12:05 | RICHARD A. JOHNSON
747 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 10:24 | 846 |  |  | 183 | [8 empty] | 0.1 | [13 empty] | ​FC was a little low so I fed st70 for 5 minutes to bring the levels up until the next feeding | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2017-09-11 10:36 | Daimon A. Boccamazzo
748 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:16 | 800 |  |  | 254 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2017-08-02 10:17 | RICHARD A. JOHNSON
749 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-07-12 11:00 | 770 | 101 | 8.2 |  | 180 | 175 | 150 | 4 | 5 | 8 | 2 | 5 | 0.6 | 0.02 | 0.05 | 1000 | 10653 | 79500 | 12 | 0 | 0 | Correct | Good | Clean | Clean | Level Okay | ​System looked great! NGG not yet connected, having issues with address provided | reedhea |  |  |  | 2017-07-12 11:13 | reedhea
750 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:14 | 1151 |  | 8.5 | 187 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 65 | 2017-06-19 07:16 | RICHARD A. JOHNSON
751 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-10 12:19 | 630 | 105 | 8.2 |  | 75 | 110 | [6 empty] | 0.02 |  |  |  | 9701.6 | 72400 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Blowdown meter is read in gallons. ST70 feed was changed to 8AM, M/W/F. H550 feed was changed to 8AM Thurs | reedhea |  |  |  | 2017-05-10 12:21 | reedhea
752 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-18 13:31 | 667 |  | 8.5 | 265 | [8 empty] | 0.2 | [13 empty] | ​st70 scheduled to feed later in the day | Daimon A. Boccamazzo | Not Adjusted |  | 71 | 2017-01-25 13:34 | Daimon A. Boccamazzo
753 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-01 13:25 | 665 |  | 8.5 | 202 | [8 empty] | 0.2 | [13 empty] | ​everything is all good, st70 schedule to fed on Friday | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-12-01 13:28 | Daimon A. Boccamazzo
754 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 15:41 | 650 | 100 | 8.6 | [9 empty] | 0.01 |  |  |  | 71200 |  |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​​ | reedhea |  |  |  | 2016-11-09 15:55 | reedhea
755 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-14 13:22 | 739 |  | 8.5 | 161 | [8 empty] | 0.2 | [13 empty] | ​found two valves that were shut. Cleaned the strainer and the conductivity sensor | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-10-24 13:25 | Daimon A. Boccamazzo
756 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-08 13:09 | 659 |  | 8.8 | 150 | [8 empty] | 0.2 | [13 empty] | ​cleaned strainer, st70 is scheduled to feed everyday at ten for thirty minutes and I have tested the tower at eight | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2016-09-08 13:13 | Daimon A. Boccamazzo
757 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-04 10:30 | 1173 |  | 8.9 | 172 | [8 empty] | 0.1 | [13 empty] | ​everything looked good besides the no flow alarm. Tower looks good as well | Daimon A. Boccamazzo | Not Adjusted |  | 78 | 2016-08-08 10:34 | Daimon A. Boccamazzo
758 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-30 10:46 | 601 | 95 | 8 | 99 | [8 empty] | 0.75 |  |  | 200000 | [10 empty] | ​​test | Jay Dahlstrom | Not Adjusted |  |  | 2016-06-30 10:49 | Jay Dahlstrom
759 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-01 14:49 | 632 |  | 8.7 | 130 | [8 empty] | 0.2 | [13 empty] | ​relay 4 feeds everyday at 10am for 30 minutes. Just need to find out if that relay is for the st70 or th h-550 and why there is only one chemical on scheduled feeding. Checked tower and everything looks good. | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-06-01 14:52 | Daimon A. Boccamazzo
760 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-18 23:15 | 705 | 131 | 8.5 |  | 250 | 270 |  |  | 2.3 | 5 | 0.18 | 0 | 0.05 | 0.308 | 0.53 |  | 5989.8 | 44700 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​ | jrojas92 |  |  |  | 2016-06-06 23:18 | jrojas92
761 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-13 12:28 | 570 |  | 8.1 | 248 | [8 empty] | 0.25 | [13 empty] | ​cleaned strainer out. Need to get a bucket up here for the system. Flow meter isn't showing alarms but the meter itself looks like there is little to no flow at all checked tower, no leaks tower all good | Daimon A. Boccamazzo | Not Adjusted |  | 78 | 2016-05-13 12:31 | Daimon A. Boccamazzo
762 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 11:27 | 769 |  | 8.4 | 288 | [8 empty] | 0 | [13 empty] | ​could not clean chemical loop strainer cause it was on way too tight. Alarm for no flow. Saw that one of the valves on the chemical loop was half way shut. Also I noticed that all three chemical pumps were turned up to 100 so I adjusted them down to 60. Also there is really low chemical in all three porta feeds need to order some ASAP. | Daimon A. Boccamazzo | Down | 60 | 67 | 2016-04-29 11:33 | Daimon A. Boccamazzo
763 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-25 21:21 | 816 | 121 | 8.5 |  | 250 | 290 |  | 0.93 | 2.6 | 1.9 | 0.32 | 0 | 0.27 | 0.444 | 2.75 |  | 5527.902 | 41253 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 21:23 | jrojas92
764 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-07 14:18 | 349 | 102 | 8.3 | 214 | [8 empty] | 0.3 | [13 empty] | ​turned on st70 20 minutes | Bob A Adams | Not Adjusted |  | 83 | 2016-04-07 14:21 | Bob A Adams
765 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-25 17:58 | 306 | 106 | 7.8 |  | 120 | 118 |  | 1.38 | 2.9 | 3.4 | 0.54 | 0 | 0.06 | 0.7831 | 2.85 |  | 5483.548 | 40922 |  |  |  | Correct | Good | Clean | Clean | Level Okay | Tower not running. ST70 tubing filled with white solids. | jrojas92 |  |  |  | 2016-05-02 18:03 | jrojas92
766 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 06:37 | 307 | 87.5 | 8.4 | 213 | [8 empty] | 0.1 | [13 empty] | ​tower was not running | Bob A Adams | Not Adjusted |  | 70 | 2016-03-29 06:41 | Bob A Adams
767 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-22 07:55 | 274 | 94.2 | 7.8 | 247 | [8 empty] | 0 | [14 empty] | Bob A Adams | Not Adjusted |  | 56.8 | 2016-03-23 07:56 | Bob A Adams
768 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-16 11:15 | 743 | 123.6 | 8.3 | 201 | [8 empty] | 0.2 | [13 empty] | ​not flowing | Bob A Adams | Not Adjusted |  | 68.9 | 2016-03-16 11:17 | Bob A Adams
769 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-22 11:39 | 698 | 104 | 8.3 | 220 | [8 empty] | 0.3 | [13 empty] | ​tower was not running | Bob A Adams | Not Adjusted |  | 67.3 | 2016-02-22 11:41 | Bob A Adams
770 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-12 14:23 | 675 | 109 | 8.5 | 289 | [8 empty] | 1.2 | [13 empty] | ​ | Bob A Adams | Not Adjusted |  | 65.8 | 2016-02-12 14:25 | Bob A Adams
771 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-05 10:41 | 690 | 99.1 | 8.3 | 170 | [8 empty] | 0.2 | [13 empty] | ​tested in no flow | Bob A Adams | Not Adjusted |  | 70.3 | 2016-02-05 10:43 | Bob A Adams
772 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 12:55 | 650 | 94.1 | 8.3 | 153 | [8 empty] | 0.1 | [14 empty] | Bob A Adams | Not Adjusted |  | 72 | 2015-12-31 13:01 | Bob A Adams
773 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 09:35 | 671 | 106.1 | 9.3 | 256 | [8 empty] | 1.5 | [14 empty] | mrh4 | Not Adjusted |  | 70.1 | 2015-12-14 09:54 | mrh4
774 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 14:16 | 641 | 143 | 8.3 |  | 210 | 264 |  | 0 | 3.8 | 1.5 | 0.54 | 0 | 0.15 | 0.6413 | 7.53 |  | 5136.756 | 38334 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-12-21 14:20 | jrojas92
775 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-09 11:25 | 654 | 101 | 9.24 | 101 | [8 empty] | 0.5 | [13 empty] | ​​ | mrh4 | Not Adjusted |  | 67.4 | 2015-11-24 11:27 | mrh4
776 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-02 14:45 | 682 | 108.3 | 9.4 | [9 empty] | 2 | [13 empty] | ​H 550 down to 8 gallons | mrh4 | Not Adjusted |  | 68.4 | 2015-11-02 14:47 | mrh4
777 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-30 14:53 | 682 | 133 | 8.5 |  | 230 | 288 |  | 0.83 | 2.1 | 1.8 | 0.31 | 0 | 0.02 |  | 1.5 |  | 5051.8 | 37700 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 14:57 | jrojas92
778 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-21 | 691 | 109.9 | 9.2 | 171 | [8 empty] | 0 | [13 empty] | ​slug fed biocides | mrh4 | Not Adjusted |  | 68.8 | 2015-10-26 09:41 | mrh4
779 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-28 18:26 | 676 | 224 | 8.2 |  | 230 | 270 |  | 0.04 | 5.7 | 10.3 | 1.21 | 0.5 | 0.83 | 0.0886 | 0.3 |  | 4609.6 | 34400 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-09-30 18:32 | jrojas92
780 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-22 11:28 | 663 | 127.9 | 9.2 | [9 empty] | 0.67 | [14 empty] | mrh4 | Not Adjusted |  |  | 2015-09-22 11:33 | mrh4
781 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-24 16:37 | 623 | 130 | 8.5 |  | 230 | 244 |  | 0.34 | 3.32 | 2.7 | 0.17 | 0.4 | 1.95 | 0.0998 | 10.4 |  | 3778.8 | 28200 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 16:40 | jrojas92
782 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-07-16 13:06 | 651 | 121 | 8.5 |  | 230 | 258 |  | 0.12 | 2.6 | 1.7 | 0.13 | 0.3 | 0.59 | 0.0829 | 0.11 |  |  | 1965 |  |  |  |  | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-08-18 13:15 | jrojas92
783 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-22 17:27 | 1044 | 112 | 8.5 |  | 240 | 378 |  | 0.82 | 1.3 | 0.1 | 0.03 | 0.2 | 0.03 | 0.0772 | 0.13 |  | 549.4 | 4100 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 17:29 | jrojas92
784 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-21 18:19 | 1142 | 6 | 8.5 |  | 250 | 394 |  | 0.08 | 0.2 | 0 | 0.05 | 1 | 0.04 | 0.0959 | 0.29 |  | 187.6 | 1400 | [7 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:22 | jrojas92
785 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-04-08 18:56 | 975 | 5.5 | 8.1 |  | 190 | 344 |  | 0.18 | 0.82 | 8.7 | 0.17 | 0 | 0.05 | 0.203 | 8.9 |  | 187.6 | 1400 | [7 empty] | Needs Filling |  | jrojas92 |  |  |  | 2015-11-14 18:58 | jrojas92
786 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 11:07 | 3090 |  |  | 201 | [8 empty] | 0 | [13 empty] | ​need to get circa pump on system ASAP. Can't fed st70 cause system has no flow. Cleaned strainer, conductivity probe, and flow meter. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2018-08-10 11:10 | Daimon A. Boccamazzo
787 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 13:12 | 1545 |  |  | 151 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2018-06-29 13:14 | RICHARD A. JOHNSON
788 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-17 13:28 | 1167 |  | 9.1 | 144 | [8 empty] | 0.5 | [13 empty] | ​still very little flow like always. Fed st70 for 30 mins to bring the levels up | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2017-01-17 13:29 | Daimon A. Boccamazzo
789 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-07 10:08 | 1181 |  | 9.4 | 174 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, conductivity sensor, and flow sensors. Free chlorine low cause there is no flow so the st70 didn't feed. After I cleaned the sensor there was enough flow that I was able to pump sone st70 into the tower | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-10-14 10:13 | Daimon A. Boccamazzo
790 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-07 07:01 | 1811 |  | 8.7 | 156 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Opened up the drain valve so fresh could be brought into the system to bring the conductivity down | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-09-08 07:04 | Daimon A. Boccamazzo
791 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-03 09:09 | 2099 |  | 8.6 | 177 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer, conductivity sensor and flow sensor. I opened up the bleed valve to drain some of the water out so the conductivity would go down, I got it down to 1100 and then put the st70 on for 30 mins to bring the free chlorine levels up. Really need to get a booster pump on the tower asap to get the water flowing a lot better. | Daimon A. Boccamazzo | Not Adjusted |  | 78 | 2016-08-04 09:14 | Daimon A. Boccamazzo
792 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-06 08:41 | 1647 |  | 8.9 | 124 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, flow sensor, conductivity sensor. Tried to bleed some water so I could get some fresh water in the tower so the conductivity could drop. I also pumped st70 in the system for about 30-45 minutes. | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-07-08 08:45 | Daimon A. Boccamazzo
793 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-31 13:08 | 860 |  | 8.3 | 196 | [8 empty] | 0 | [13 empty] | ​consistent no flow alarms affecting the system and the chemical treatment. Need booster pump on the tower asap. Also need to get spicket fixed so I can turn the valves on so the system can try and feed some chemical into the tower | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-05-31 13:12 | Daimon A. Boccamazzo
794 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-22 23:55 | 1050 | 116 | 8.6 |  | 390 | 396 |  |  | 0.8 | 0 | 2.38 | 0 | 0 | 0.059 | 0.11 |  | 26766 | 2426 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​No flow, dirty water. Manually BD until conductivity of 700. | jrojas92 |  |  |  | 2016-06-06 23:59 | jrojas92
795 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 07:14 | 1082 |  | 8.8 | 223 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, will definitely need to be cleaned next time around. Relay 4 feeds every day for 19 minutes at 12pm and relay 5 pumps every day for 5 minutes at 5pm. should probably be changed. Need booster pump on this tower cause I'm getting consistent no flow alarms | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-05-13 07:19 | Daimon A. Boccamazzo
796 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-28 22:33 | 994 | 242 | 8.6 |  | 360 | 394 |  | 0.23 | 2.8 | 6.2 | 5.94 | 0.6 | 0 | 0.268 | 0.17 |  | 26088 | 2424 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 22:37 | jrojas92
797 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-28 11:40 | [26 empty] | ​alarms for no flow and high conductivity, saw that the taser pump was almost all the way up to 100 and adjusted it down to 60 also I cleaned out the chemical loop filter (it was pretty clogged and dirt). Need to get a booster pump on the tower Asa's to help with flow and chemical treatment | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-28 11:43 | Daimon A. Boccamazzo
798 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-25 07:03 | [26 empty] | ​alarms for no flow, and high conductivity, Don needs to get a booster pump in here asap to help the flow of the entire tower and chemical system. Also need to get a bucket in the mech room for water messes | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-26 07:08 | Daimon A. Boccamazzo
799 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-15 14:35 | 615 | 158 | 7.9 | [9 empty] | 4.9 | [13 empty] | ​once I got to the tower and tried to take a sample I noticed that there was no water coming out. Then I icsolated the catch screen cup and cleaned it out and once I did that and put it back on, then the water started running. Also when I got there I noticed that there were alarms going off cause of the flow. I also noticed when I got there that the 3dt222 ppm was at zero, I was going to make adjustments but once I got the water going then it showed that there was 3dt222 pumping through the system | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-15 14:42 | Daimon A. Boccamazzo
800 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-14 14:47 | 650 | 17.1 | 7.5 | 330 | [8 empty] | 0 | [13 empty] | ​​cleaned out screen and noticed that after putting it back on and turning the valves on it almost immediately got a bunch of gunk in it. Also was not getting very much flow at all even after cleaning the flow sensor | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-14 14:55 | Daimon A. Boccamazzo
801 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-06 11:57 | 716 | 250 | 8.4 | 190 | [8 empty] | 0 | [13 empty] | ​​no flow. Tower needs booster pump | Bob A Adams | Not Adjusted |  | 78 | 2016-04-06 11:59 | Bob A Adams
802 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-29 20:31 | 787 | 9 | 8.3 |  | 180 | 160 |  | 1.18 | 1.5 | 0.4 | 3.12 | 0.4 | 0 | 0.454 | 0.43 |  | 85675 | 2423 |  |  |  | Correct |  | Clean | Clean | Level Okay | ​Dirty water. | jrojas92 |  |  |  | 2016-06-06 20:36 | jrojas92
803 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 08:23 | 735 | 250 | 8.4 | 290 | [8 empty] | 0 | [13 empty] | ​Trasar read too high | Bob A Adams | Not Adjusted |  | 75 | 2016-03-25 08:27 | Bob A Adams
804 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 10:33 | 720 | 183.5 | 8.3 | 291 | [8 empty] | 0.4 | [14 empty] | Bob A Adams | Not Adjusted |  | 72 | 2016-03-10 10:34 | Bob A Adams
805 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 14:06 | 605 | 250 | 7.5 | 316 | [8 empty] | 0 | [13 empty] | ​TRASAR only read Hi Conc. Water is still not flowing. Reported problems to Nalco Beth S. | Bob A Adams | Not Adjusted |  | 73.5 | 2016-02-08 14:10 | Bob A Adams
806 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-25 13:50 | 721 |  | 7.1 | 225 | [8 empty] | 0 | [13 empty] | ​​Trasar read Hi conc. Still no flow through chemical loop even though tower is running. | Bob A Adams | Not Adjusted |  | 72.7 | 2016-01-25 13:53 | Bob A Adams
807 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-06 13:48 | 687 | 151 | 8.5 | 200 | [8 empty] | 0.3 | [13 empty] | ​still having flow issue. Cleaned strainer and flow probe. | Bob A Adams | Not Adjusted |  | 68 | 2016-01-06 13:50 | Bob A Adams
808 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:51 | 602 | 8 | 8.4 | 289 | [8 empty] | 1.2 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 87 | 2015-12-31 07:54 | Bob A Adams
809 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 14:11 | 82.5 | 44.8 | 8.8 |  | 40 | 38 |  | 0.3 | 1.4 | 0 | 0.41 | 0.6 | 0.77 | 0.0664 | 0.04 | [6 empty] | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-12-22 14:13 | jrojas92
810 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-14 15:31 | 674 | 324 | 8.4 |  | 190 | 200 |  | 0.19 | 8.1 | 13.3 | 4.7 | 1.3 | 0.01 | 0.0501 | 0.09 | [6 empty] | Correct | Good | Clean | Clean |  | ​​Only 2 gal of 3DT222 left. | jrojas92 |  |  |  | 2015-11-14 15:33 | jrojas92
811 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-20 07:45 | 739 | 399 | 8.6 | 150 | [8 empty] | 0.1 | [14 empty] | Bob A Adams | Not Adjusted |  | 78 | 2015-10-26 07:48 | Bob A Adams
812 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-12 08:22 | 582 | 399 | 8.5 | 158 | [8 empty] | 0.4 | [14 empty] | Bob A Adams | Not Adjusted |  | 78.9 | 2015-10-26 08:24 | Bob A Adams
813 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-29 19:13 | 657 | 401 | 8.5 |  | 200 | 208 |  | 0 | 9.6 | 15.9 | 4.8 | 1.7 | 0.01 | 0.0731 | 0.16 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​There was fouling/scaling of the fluorometer that was causing it to read lower Trasar level than it actually is. Tried cleaning with pipe brush, but did not help by much. | jrojas92 |  |  |  | 2015-09-30 19:19 | jrojas92
814 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:41 | 109.4 |  |  | 146 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2018-08-30 11:42 | RICHARD A. JOHNSON
815 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 11:10 | 124 |  |  | 166 | [8 empty] | 0.2 | [13 empty] | ​FC levels are okay for now, tower will feed st70 tomorrow. Need to figure out how to stop the tower from draining water out for 2 hours. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2018-08-10 11:14 | Daimon A. Boccamazzo
816 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-28 13:17 | 64.42 |  |  | 162 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 65 | 2018-06-29 13:20 | RICHARD A. JOHNSON
817 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-25 13:28 | 70.85 |  |  | 134 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 64 | 2018-04-30 13:29 | RICHARD A. JOHNSON
818 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-21 10:08 | 111.4 |  |  | 207 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 47 | 2018-02-23 10:09 | RICHARD A. JOHNSON
819 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-27 13:52 | 105 |  |  | 197 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 52 | 2017-12-29 13:54 | RICHARD A. JOHNSON
820 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-19 10:39 | 110 |  |  | 179 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2017-10-23 10:40 | RICHARD A. JOHNSON
821 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:25 | 130 |  |  | 220 | [8 empty] | 0.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2017-08-24 08:27 | RICHARD A. JOHNSON
822 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:22 | 131 |  |  | 251 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 75 | 2017-08-02 10:23 | RICHARD A. JOHNSON
823 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-18 13:10 | 187 |  | 9.5 | 164 | [8 empty] | 0.4 | [13 empty] | ​everything is as usual. Starting to see a increase in the chlorine levels in a good way | Daimon A. Boccamazzo | Not Adjusted |  | 55 | 2017-01-25 13:13 | Daimon A. Boccamazzo
824 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-07 10:15 | 672 |  | 9 | 176 | [8 empty] | 0.1 | [13 empty] | ​no flow alarm. Strainer is all good | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2016-10-14 10:16 | Daimon A. Boccamazzo
825 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-07 07:05 | 328 |  | 8.9 | 148 | [8 empty] | 0.5 | [13 empty] | ​cleaned strainer, flow and conductivity sensors. Conductivity still a little bit low but there are no alarms for it. But everything else looks good. | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2016-09-08 07:07 | Daimon A. Boccamazzo
826 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-04 10:09 | 294 |  | 8.9 | 151 | [8 empty] | 0 | [13 empty] | ​cleaned conductivity sensor, strainer, and flow sensor. Not sure if fans weren't running at all or if they just weren't running at the time that I got there. Bleed valve is shut but can't tell if it is leaking or not cause the drain pipe coming from the tower is connected to the roof drain pipe | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-08-08 10:20 | Daimon A. Boccamazzo
827 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-04 08:57 | 294 |  | 8.9 | 151 | [8 empty] | 0 | [13 empty] | ​cleaned conductivity sensor, flow sensor and strainer. Not sure if the fans to circulate the water doesn't run or if it just wasn't running when I got there to test the tower. also even though the bleed valve is shut I can't tell if the valve is leaking by or not cause the drain pipe is attached to the roof drain | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-08-04 09:03 | Daimon A. Boccamazzo
828 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-07 08:46 | 235 |  | 8.8 | 174 | [8 empty] | 0.1 | [13 empty] | ​chemicals are there but not hooked. One of the pumps is trying to run but it is not hooked up to any kind of chemical and stops because of that. Using ch2o chemical on the other pump. Cleaned strainer, flow sensor, and conductivity sensor | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-07-08 08:50 | Daimon A. Boccamazzo
829 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-31 13:13 | 160 |  | 8.6 | 192 | [8 empty] | 0.1 | [13 empty] | ​Robert from Nalco is finishing up the new controller install for the tower and I am sure that's why all the readings I got were pretty low. Need to get chemicals up here asap so they can be hooked up and the tower can start feeding chemical into the system | Daimon A. Boccamazzo | Not Adjusted |  | 71 | 2016-05-31 13:16 | Daimon A. Boccamazzo
830 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 13:10 | 293 |  | 8.6 | 269 | [8 empty] | 1.4 | [13 empty] | ​low alarm on cooling tower controller, output timeout on orp/ph controller. Old walchem controller not sure how to use it. Need bucket of ch2o posca up here | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-05-12 13:14 | Daimon A. Boccamazzo
831 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 08:14 | 88 |  | 6.5 | 330 | [8 empty] | 0.1 | [13 empty] | ​still has old Walchem controllers. Showing low conductivity alarm also showing output timeout alarm. Not sure how to work the Walchem controls, would like to be taught asap in case I run into problems like this again | Daimon A. Boccamazzo | Not Adjusted |  | 56 | 2016-04-29 08:18 | Daimon A. Boccamazzo
832 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-24 13:50 | 620 | 8 | 8.4 | 203 | [8 empty] | 0.3 | [14 empty] | Bob A Adams | Not Adjusted |  | 88 | 2016-02-24 13:52 | Bob A Adams
833 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 11:27 | 390 | 4 | 8.3 | 118 | [8 empty] | 0 | [13 empty] | ​Posca in range. can't keep bromine primed in cold temperatures. Bleed solenoid had debri in it letting water drip out lowering conductivity. | Bob A Adams | Not Adjusted |  | 85 | 2016-02-08 11:31 | Bob A Adams
834 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-25 13:48 | 691 | 6 | 8.6 | 163 | [8 empty] | 0 | [13 empty] | ​Posca in range. Bromine pump lost prime due to cold weather. | Bob A Adams | Not Adjusted |  | 77 | 2016-01-25 13:49 | Bob A Adams
835 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-04 14:28 | 650 | 4 | 8.5 | 112 | [8 empty] | 0 | [13 empty] | ​Posca in range. Bromine continues to stop pumping due to the chemical being too cold. | Bob A Adams | Not Adjusted |  | 59 | 2015-12-04 14:32 | Bob A Adams
836 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-09 08:11 | 1100 | 4 | 8.7 | 350 | [8 empty] | 2 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 76 | 2015-10-26 08:16 | Bob A Adams
837 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 10:59 | 1891 |  |  | 460 | [8 empty] | 8.8 | [13 empty] | ​everything is so high because Tuesday I put three bottles of bleach in the tower | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2017-09-11 11:05 | Daimon A. Boccamazzo
838 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:20 | 1140 |  |  | 246 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 73 | 2017-08-02 10:21 | RICHARD A. JOHNSON
839 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:04 | 774 |  | 9 | 570 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 54 | 2017-06-19 07:07 | RICHARD A. JOHNSON
840 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-20 14:41 | 3786 |  | 9.1 | 250 | [8 empty] | 0.2 | [13 empty] | ​not cycling water through due to cold weather. Poured one bottle of bleach in to bring the FC levels up | Daimon A. Boccamazzo | Not Adjusted |  | 51 | 2017-01-25 14:45 | Daimon A. Boccamazzo
841 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-01 13:34 | 2950 |  | 9 | 230 | [8 empty] | 2.2 | [13 empty] | ​there was bleach left over from my lasting testing and I think that's why the conductivity was so high | Daimon A. Boccamazzo | Not Adjusted |  | 45 | 2016-12-01 13:37 | Daimon A. Boccamazzo
842 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-18 13:42 | 1996 |  | 9 | 163 | [8 empty] | 0.1 | [13 empty] | ​poured tree bottles of bleach into the tower to bring the free chlorine levels up | Daimon A. Boccamazzo | Not Adjusted |  | 51 | 2016-10-24 13:47 | Daimon A. Boccamazzo
843 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-08 13:17 | 1280 |  | 8.6 | 165 | [8 empty] | 0.3 | [13 empty] | ​put 2.5 bottles of bleach into the tower to bring the free chlorine levels up | Daimon A. Boccamazzo | Not Adjusted |  | 58 | 2016-09-08 13:18 | Daimon A. Boccamazzo
844 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-18 10:29 | 1156 |  | 8.9 | 134 | [8 empty] | 0.1 | [13 empty] | ​dumped two bottles of bleach into the tower to bring the free chlorine levels up | Daimon A. Boccamazzo | Not Adjusted |  | 62 | 2016-07-18 10:31 | Daimon A. Boccamazzo
845 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-16 10:49 | 1716 |  | 9.1 | 625 | [8 empty] | 1.17 | [13 empty] | ​will definitely need 2 bottles of bleach next time around | Daimon A. Boccamazzo | Not Adjusted |  | 53 | 2016-05-16 10:50 | Daimon A. Boccamazzo
846 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-13 07:53 | [12 empty] | 8.8 | [13 empty] | ​levels are above 8 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-13 07:54 | Daimon A. Boccamazzo
847 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 08:50 | [12 empty] | 0.04 | [13 empty] | ​poured three bottles of bleach in the tower. Let pumps run for a little bit and then tested again and got .05 and then grabbed another sample and got .2. Reason why the second test was so low was cause we had poured three bottles of bleach in the system. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-12 08:55 | Daimon A. Boccamazzo
848 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-08 14:09 | 162 | 0 | 8.9 | 280 | [8 empty] | 0 | [14 empty] | Bob A Adams | Not Adjusted |  | 58 | 2016-04-08 14:10 | Bob A Adams
849 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-28 06:49 | 140 | 0 | 8.8 | 233 | [8 empty] | 0.1 | [13 empty] | ​no chemical system | Bob A Adams | Not Adjusted |  | 53 | 2016-03-29 06:51 | Bob A Adams
850 | 4057 | 4057-Condenser_Water-UW | Condenser Water | UW | 2015-12-14 07:46 | 845 | 8 | 8.5 | 242 | [8 empty] | 0.5 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 71 | 2015-12-31 07:48 | Bob A Adams
851 | 4057 | 4057-Condenser_Water-UW | Condenser Water | UW | 2015-12-11 07:12 | 817 | 8 | 8.5 | 232 | [8 empty] | 0.3 | [13 empty] | ​free chlorine in range. Posca in range | Bob A Adams | Not Adjusted |  | 70.3 | 2015-12-31 07:17 | Bob A Adams
852 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-24 10:14 | 3069 |  |  | 251 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-10-01 10:15 | RICHARD A. JOHNSON
853 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:40 | 3408 |  |  | 163 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-08-30 11:40 | RICHARD A. JOHNSON
854 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 10:59 | 2662 |  |  | 174 | [8 empty] | 0.3 | [13 empty] | ​porta feed for st70 still needs to be replaced. Y strainer on bleed valve was cleaned so system should be able to bleed some water when conductivity gets too high | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2018-08-10 11:03 | Daimon A. Boccamazzo
855 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 06:56 | 2578 |  |  | 160 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-07-03 06:57 | RICHARD A. JOHNSON
856 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-23 13:23 | 1682 |  |  | 182 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-04-30 13:24 | RICHARD A. JOHNSON
857 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-22 10:10 | 1774 |  |  | 131 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2018-02-23 10:11 | RICHARD A. JOHNSON
858 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-28 13:58 | 2171 |  |  | 221 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  |  | 2017-12-29 13:58 | RICHARD A. JOHNSON
859 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-18 10:41 | 1343 |  |  | 306 | [8 empty] | 0.5 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2017-10-23 10:42 | RICHARD A. JOHNSON
860 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:17 | 1992 |  |  | 177 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-24 08:18 | RICHARD A. JOHNSON
861 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 07:33 | 1631 |  |  | 168 | [8 empty] | 0.2 | [13 empty] | ​tested on an off day | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2017-08-02 07:35 | RICHARD A. JOHNSON
862 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-17 13:21 | 1146 |  | 8.8 | 135 | [8 empty] | 0.1 | [13 empty] | ​Free chlorine is low because it is in between feeding cycles | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2017-01-17 13:25 | Daimon A. Boccamazzo
863 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-29 11:45 | 2359 |  | 8.9 | 173 | [8 empty] | 0 | [13 empty] | ​blowdown was on when I got there. Adjusted st70 pump to 80 instead of 60 | Daimon A. Boccamazzo | Up | 80 | 69 | 2016-11-29 11:48 | Daimon A. Boccamazzo
864 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-06 09:21 | 2170 |  | 9.2 | 177 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer and conductivity sensor. Also fed chemical for 30 minutes | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-10-14 09:24 | Daimon A. Boccamazzo
865 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-06 14:42 | 2168 |  | 8.7 | 152 | [8 empty] | 0.2 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Turned bleed valve on for 15mins to bring the conductivity levels down. Also found a shut valve, so I opened it and that solved the no flow alarm | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-09-06 14:45 | Daimon A. Boccamazzo
866 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-02 11:35 | 1755 |  | 8.8 | 147 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer and conductivity sensor. Need to find out why the bleed valve times out. when I got there the bleed valve was open but the conductivity was staying in that 1600 to almost 1800 range. | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-08-02 11:39 | Daimon A. Boccamazzo
867 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-29 08:33 | 1219 |  | 8.9 | 207 | [8 empty] | 1.2 | [13 empty] | ​st70 was pumping when I got there, didn't clean strainer cause i didn't want to disrupt the feeding chemical. Strainer, flow sensor and conductivity sensor will need to be cleaned next time around | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-07-08 08:37 | Daimon A. Boccamazzo
868 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-27 11:58 | 1332 |  | 8.9 | 180 | [8 empty] | 0.3 | [13 empty] | ​need to check the calibration for the conductivity on the controller cause it is reading 1200 and my meter is reading 1332. Reasoning for the free chlorine being low is because it has not feed st70 into the tower sense Wednesday at 1pm for 2 hours | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-05-27 12:04 | Daimon A. Boccamazzo
869 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-21 09:18 | [12 empty] | 0.5 | [13 empty] | ​​tested the tower just to make sure things were good and back to normal. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-23 09:20 | Daimon A. Boccamazzo
870 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-20 13:57 | 1097 | [11 empty] | 4.2 | [13 empty] | ​almost 2 hours after second reading (1:15) still above 2ppm protocol and st70 was feeding into the system as I was leaving. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-20 14:01 | Daimon A. Boccamazzo
871 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-20 13:55 | 1100 | [11 empty] | 5.1 | [13 empty] | ​3 hours after first free chlorine test (11:30) still above 2ppm | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-20 13:56 | Daimon A. Boccamazzo
872 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-20 13:46 | 1087 | [11 empty] | 8.8 | [13 empty] | ​start of the protocol at 8:30 am. Feed 2 gallons of 7341 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-20 13:51 | Daimon A. Boccamazzo
873 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-20 09:16 | [12 empty] | 6.9 | [13 empty] | ​​well above range of protocol (2ppm for 8hrs) turned blowdown valve back to auto. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-23 09:18 | Daimon A. Boccamazzo
874 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-10 14:53 | 791 |  | 8.7 | 247 | [8 empty] | 0.17 | [13 empty] | ​cleaned out chemical loop strainer. Need to check calibration on the controller for ph and orp. On the controller ph is reading 10.14 and my meter got 8.7. Orp is reading 319 and my meter got 247. | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-05-10 14:57 | Daimon A. Boccamazzo
875 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-25 11:20 | 680 |  | 8.2 | 230 | [8 empty] | 0.1 | [13 empty] | ​noticed when I walked up to the controller the ph was a little high it was reading 9.56. When I tested for the ph levels I got 8.2 but at the same time the ph level on the controller was reading 8.5. So I'm not sure if my ph level meter needs to be calibrated or something else is the problem. The chemical loop strainer looked good and did not need to be cleaned out. Also I tested for the free chlorine levels and got .1 the I tested it a second time a got 0 so I went at looked at the porta feed and see if there is a problem with the st70 and I did notice that the tube going to the pump from the bottom of the porta feed had some chemical gunk on it and found that the connecting fasteners were loose so I tightened those up. I was also expecting to have a little bit of a higher reading on the free chlorine level because Julio was pumping st70 into the system over the weekend. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-25 11:31 | Daimon A. Boccamazzo
876 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-04 12:48 | 898 | 0 | 8.4 | 310 | [8 empty] | 1 | [13 empty] | ​pumped st70 into system hand fed. | Bob A Adams | Not Adjusted |  | 68 | 2016-04-04 12:51 | Bob A Adams
877 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 10:29 | 7299 | 0 | 8.5 | 224 | [8 empty] | 0.2 | [13 empty] | ​waiting for Nalco to turn on new system | Bob A Adams | Not Adjusted |  | 65 | 2016-03-10 10:31 | Bob A Adams
878 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-09 14:42 | 809 | 6 | 8.5 | 288 | [8 empty] | 0.8 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 72 | 2016-02-09 14:44 | Bob A Adams
879 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-28 14:14 | 830 | 8 | 8.5 | 285 | [8 empty] | 0.8 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 69 | 2016-01-28 14:15 | Bob A Adams
880 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-12 14:24 | 798 | 8 | 8.5 | 312 | [8 empty] | 1.1 | [14 empty] | Bob A Adams | Not Adjusted |  | 71 | 2016-01-12 14:25 | Bob A Adams
881 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-06 13:44 | 868 | 10 | 8.4 | 212 | [8 empty] | 0.1 | [13 empty] | ​Posca in range. Calibrated Temp. Cleaned sensors | Bob A Adams | Not Adjusted |  | 71 | 2016-01-06 13:46 | Bob A Adams
882 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-30 13:56 | 861 | 6 | 8.6 | 201 | [8 empty] | 0.4 | [13 empty] | ​Posca in range. Chlorine in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 72 | 2015-11-30 13:58 | Bob A Adams
883 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-18 06:55 | 848 | 8 | 8.5 | 292 | [8 empty] | 1.1 | [13 empty] | ​Posca in range. Cleaned sensors ​ | Bob A Adams | Not Adjusted |  | 70 | 2015-11-20 06:57 | Bob A Adams
884 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-12 14:03 | 845 | 6 | 8.6 | 299 | [8 empty] | 0.5 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 70.8 | 2015-11-16 14:06 | Bob A Adams
885 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-28 07:02 | 701 | 4 | 8.5 | 255 | [8 empty] | 1.5 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 73 | 2015-11-03 07:04 | Bob A Adams
886 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-08 06:36 | 630 | 6 | 8.4 | 190 | [8 empty] | 0.3 | [13 empty] | ​Posca & free chlorine in range​ | Bob A Adams | Not Adjusted |  | 73 | 2015-10-12 06:39 | Bob A Adams
887 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-27 14:47 | 645 |  | 8.6 | [23 empty] | OPR - 310 TWO - .3 OP - 8​ | mrh4 | Not Adjusted |  | 68.6 | 2015-09-23 14:47 | Jay Dahlstrom
888 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-17 14:46 | 654 |  | 8.5 | [23 empty] | ​​OPR - 247 TWO - .5 OP - 6 | mrh4 | Not Adjusted |  | 69 | 2015-09-23 14:47 | Jay Dahlstrom
889 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-10 14:45 | 608 |  | 8.6 | [23 empty] | OPR - 150 TWO - .2 OP - 8​ | mrh4 | Not Adjusted |  | 67 | 2015-09-23 14:46 | Jay Dahlstrom
890 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-04 14:44 | 645 |  | 8.5 | [23 empty] | OPR - 199 TWO - .4 OP - 6​ | mrh4 | Not Adjusted |  | 68 | 2015-09-23 14:45 | Jay Dahlstrom
891 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-24 14:44 | 651 |  | 8.6 | [23 empty] | ​​OPR - 174 TWO - .4 OP - 6 | mrh4 | Not Adjusted |  | 69.2 | 2015-09-23 14:44 | Jay Dahlstrom
892 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-30 | 641 |  | 8.5 | [23 empty] | OPR - 110 TWO - 0 OP - 6​ | mrh4 | Not Adjusted |  | 69 | 2015-09-23 14:44 | Jay Dahlstrom
893 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-02 14:42 | 610 |  | 8.5 | [23 empty] | OPR - 120 TWO - .5 OP - 8​ | mrh4 | Not Adjusted |  | 69.2 | 2015-09-23 14:43 | Jay Dahlstrom
894 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-20 14:41 | 600 |  | 8.6 | [23 empty] | ​OPR - 120 TWO - 0 OP - 8​ | mrh4 | Not Adjusted |  | 69.9 | 2015-09-23 14:42 | Jay Dahlstrom
895 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-11 14:41 | 661 |  | 8.5 | [23 empty] | ​OPR - 232 TWO - 0 OP - 8 | mrh4 | Not Adjusted |  | 69.8 | 2015-09-23 14:41 | Jay Dahlstrom
896 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-06 14:40 | 641 |  | 8.5 | [23 empty] | ​OPR - 251 TWO - .6 OP - 6 | mrh4 | Not Adjusted |  | 69 | 2015-09-23 14:41 | Jay Dahlstrom
897 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 14:39 | 655 |  | 8.6 | [23 empty] | ​​OPR - 278 TWO - .8 OP - 6 | mrh4 | Not Adjusted |  | 68.8 | 2015-09-23 14:40 | Jay Dahlstrom
898 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 14:38 | 712 |  | 8.5 | [23 empty] | ​OPR - 131 TWO - 0 OP - 6 | mrh4 | Not Adjusted |  | 69.2 | 2015-09-23 14:39 | Jay Dahlstrom
899 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-15 13:40 | 593 |  | 7.7 | [23 empty] | ​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 21.4 | 2015-09-21 13:40 | Jay Dahlstrom
900 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-18 14:32 | 389 |  | 9.2 | [23 empty] | ​OPR - 199 TWO - 0 OP - 4​ | mrh4 | Not Adjusted |  | 69.6 | 2015-09-23 14:33 | Jay Dahlstrom
901 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-17 14:31 | 628 |  | 8.5 | [23 empty] | ​​OPR - 291 TWO - .8 OP - 6 | mrh4 | Not Adjusted |  | 65 | 2015-09-23 14:32 | Jay Dahlstrom
902 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-07 14:30 | 600 |  | 8.6 | [23 empty] | ​​ORP - 283 TWO - .6 OP - 6 | mrh4 | Not Adjusted |  | 69.4 | 2015-09-23 14:31 | Jay Dahlstrom
903 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-26 14:29 | 677 |  | 8.2 | [23 empty] | ​​OPR - 196 TWO - .3 OP - 4 | mrh4 | Not Adjusted |  | 70 | 2015-09-23 14:30 | Jay Dahlstrom
904 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-22 14:29 | 497 |  | 8.5 | [23 empty] | ORP - 234 TWO - .4 OP - 4​ | mrh4 | Not Adjusted |  | 66.6 | 2015-09-23 14:29 | Jay Dahlstrom
905 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-06 14:27 | 610 |  | 8.6 | [23 empty] | ​OPR - 157 TWO - 0 OP - 6 | mrh4 | Not Adjusted |  | 68.3 | 2015-09-23 14:28 | Jay Dahlstrom
906 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-17 10:27 | 1027 |  |  | 152 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 59 | 2018-10-01 10:28 | RICHARD A. JOHNSON
907 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 11:08 | 898.8 |  |  | 189 | [8 empty] | 2.3 | [13 empty] | ​Tower was feeding ST70 at time of the test | RICHARD A. JOHNSON | Not Adjusted |  | 79 | 2018-07-30 11:09 | RICHARD A. JOHNSON
908 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-18 10:26 | 761.1 |  |  | 149 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-05-31 10:27 | RICHARD A. JOHNSON
909 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-23 07:53 | 689.2 |  |  | 146 | [8 empty] | 1.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 59 | 2018-04-02 07:55 | RICHARD A. JOHNSON
910 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 08:24 | 750 |  |  | 285 | [8 empty] | 0.5 | [13 empty] | ​system is all good. Feeding st70 while I tested system | Daimon A. Boccamazzo | Not Adjusted |  | 59 | 2018-03-16 08:32 | Daimon A. Boccamazzo
911 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-30 13:18 | 577 |  |  | 228 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2018-02-01 13:19 | RICHARD A. JOHNSON
912 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-21 12:01 | 640 |  |  | 199 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2017-12-04 12:03 | RICHARD A. JOHNSON
913 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 10:17 | 796 |  |  | 190 | [8 empty] | 0.3 | [13 empty] | ​good FC reading on off day of feeding | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2017-09-11 10:22 | Daimon A. Boccamazzo
914 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:14 | 770 |  |  | 233 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 81 | 2017-08-02 10:15 | RICHARD A. JOHNSON
915 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:10 | 858 |  | 9.21 | 220 | [8 empty] | 8.8 | [13 empty] | ​tower was feeding during test | RICHARD A. JOHNSON | Not Adjusted |  | 73 | 2017-06-19 07:13 | RICHARD A. JOHNSON
916 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-10 12:42 | 800 | 101 | 8.4 |  | 150 | 130 | [6 empty] | 0.61 |  |  |  |  | 25073.8 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​​ST70 feed changed to M/W/F, 8Am, 270min feeds, H550 changed to thu, 8am, 120min feed | reedhea |  |  |  | 2017-05-10 12:50 | reedhea
917 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-18 13:22 | 749 |  | 8.4 | 254 | [8 empty] | 0.1 | [13 empty] | ​no flow cause tower hardly runs due to low temps lately. St70 was scheduled to feed at 1:25 for 4 hours. | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2017-01-25 13:28 | Daimon A. Boccamazzo
918 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-01 13:21 | 684 |  | 8.3 | 198 | [8 empty] | 0.4 | [13 empty] | ​there was no flow when I got there cause the tower was not running do to the fact that there was no demand for it | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-12-01 13:24 | Daimon A. Boccamazzo
919 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 15:42 | 1710 | 130 | 7.9 | [9 empty] | 0.03 | [8 empty] | Correct | Good | Clean | Dirty | Level Okay | Controller blowdown was in manual off setting on arrival. Placed back into auto. Cleaned strainer. | reedhea |  |  |  | 2016-11-09 15:57 | reedhea
920 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-07 10:24 | 877 |  | 9 | 173 | [8 empty] | 0.1 | [13 empty] | ​everything is all good, no alarms. St70 was feeding when I got to the location and I didn't want to disrupt it to clean the strainer. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-10-14 10:29 | Daimon A. Boccamazzo
921 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-07 07:12 | 895 |  | 8.6 | 163 | [8 empty] | 1.4 | [13 empty] | ​everything all good. Strainer may need to cleaned next time around but that's the only thing. | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-09-08 07:16 | Daimon A. Boccamazzo
922 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-04 10:24 | 920 |  | 8.7 | 177 | [8 empty] | 0.2 | [13 empty] | ​strainer is good, I checked the timer for st70 and it is set for 4 hours at 60% every Monday, Wednesday, and Friday. I'm not sure how to change the timer so I left the 4 hour timer feeding on there but just adjusted the pumps down to 40% until I know how to change the time. And the was an alarm for the #1corrosion probe being high but I'm assuming the reason why is cause of all the st70 that gets pumped into the system | Daimon A. Boccamazzo | Not Adjusted |  | 84 | 2016-08-08 10:29 | Daimon A. Boccamazzo
923 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-06-30 08:57 | 652 | 99 | 7.5 | [8 empty] | 3.001 | 0.75 | 0.75 | [12 empty] | ​test | Jay Dahlstrom |  |  |  | 2016-06-30 08:59 | Jay Dahlstrom
924 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-01 09:11 | 362 |  | 8.5 | 185 | [8 empty] | 0.3 | [13 empty] | ​st70 is scheduled to pump at 1pm everyday for an hour and when I went there at 2:30 is was saying that it still had 20 mins left to pump and it said bleed valve lockout. Also the st70 pump doesn't seem to when it was saying it was feeding the chemical. | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2016-06-01 09:15 | Daimon A. Boccamazzo
925 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-18 23:23 | 469 | 168 | 8.4 |  | 190 | 206 |  |  | 4.1 | 10.7 | 0.77 | 0.7 | 0 | 0.084 | 0.5 |  | 897666 | 3170 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​The pump head tube for ST70 peristaltic pump needs replacing, not drawing chemical. | jrojas92 |  |  |  | 2016-06-06 23:29 | jrojas92
926 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-13 12:22 | 505 |  | 8.6 | 234 | [8 empty] | 0.05 | [13 empty] | ​need to get a new chemical loop strainer asap, it's falling apart. Scrubbed some of the milkyness off the chemical loop strainer enclosure. No alarms. Chemicals all good | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-05-13 12:27 | Daimon A. Boccamazzo
927 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 10:11 | 360 |  | 7.93 | 290 | [8 empty] | 0 | [13 empty] | ​chemical loop strainer is really dirty, has a white substance in it, I have a picture of it as well, there was an alarm for low conductivity. Also I noticed that the stabrex chemical pump was at 100 so I adjusted it down to 60 | Daimon A. Boccamazzo | Not Adjusted |  | 55 | 2016-04-29 10:16 | Daimon A. Boccamazzo
928 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-25 21:57 | 397 | 162 | 8.3 |  | 160 | 180 |  | 1.27 | 4.2 | 8 | 0.98 | 0.7 | 0 | 0.111 | 0.33 |  | 897666 | 3170 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 22:01 | jrojas92
929 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-06 14:20 | 276 | 135.1 | 8.2 | 232 | [8 empty] | 0.5 | [14 empty] | Bob A Adams | Not Adjusted |  | 62 | 2016-04-06 14:22 | Bob A Adams
930 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-25 19:52 | 239 | 158 | 7.9 |  | 90 | 110 |  | 0.23 | 4.5 | 8.4 | 1.95 | 0.4 | 0.17 | 0.159 | 0.55 |  | 897666 | 3170 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 19:58 | jrojas92
931 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 08:19 | 242 | 140.5 | 8.7 | 214 | [8 empty] | 0.1 | [13 empty] | ​calibrated cond and Orp | Bob A Adams | Not Adjusted |  | 56.2 | 2016-03-25 08:23 | Bob A Adams
932 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-22 11:36 | 306 | 152 | 8.5 | 309 | [8 empty] | 0.6 | [13 empty] | ​Cooling tower drained do to chiller issues | Bob A Adams | Not Adjusted |  | 47.7 | 2016-02-22 11:38 | Bob A Adams
933 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-12 08:34 | 600 | 169 | 8.7 | 356 | [8 empty] | 7.6 | [13 empty] | ​Bleed solenoid is turned off and conductivity is not raising too high. | Bob A Adams | Not Adjusted |  | 58.3 | 2016-02-12 08:38 | Bob A Adams
934 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-05 11:16 | 544 | 151.6 | 8.3 | 410 | [8 empty] | 6.8 | [13 empty] | ​calibrated conductivity | Bob A Adams | Not Adjusted |  | 57.6 | 2016-02-05 11:17 | Bob A Adams
935 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-28 14:17 | 345 | 161 | 8.6 | 333 | [8 empty] | 1.6 | [14 empty] | Bob A Adams | Not Adjusted |  | 59 | 2016-01-28 14:18 | Bob A Adams
936 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-27 14:12 | 299 | 94.4 | 8.6 | 235 | [8 empty] | 1.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 57 | 2016-01-28 14:14 | Bob A Adams
937 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-15 08:57 | 267 | 162.1 | 8.5 | 165 | [8 empty] | 1.3 | [13 empty] | ​Small blow by stream. 3D Trasar is at order level | Bob A Adams | Not Adjusted |  |  | 2016-01-15 08:59 | Bob A Adams
938 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-30 14:49 | 325 | 155 | 8.3 | 177 | [8 empty] | 0 | [13 empty] | ​stabrex is empty | Bob A Adams | Not Adjusted |  | 53 | 2015-12-30 14:52 | Bob A Adams
939 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 09:25 | 603 | 132.7 | 9.3 | 324 | [8 empty] | 2.1 | [13 empty] | ​Portafeed for ST 70 is empty. Need to reorder ASAP | mrh4 | Not Adjusted |  | 60.6 | 2015-12-14 09:31 | mrh4
940 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 14:23 | 600 | 182 | 8.5 |  | 120 | 120 |  | 0.4 | 5.3 | 8.2 | 1.63 | 0.7 | 10.2 | 0.1484 | 0.87 |  | 897532 | 3170 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​ST70 chemical is low (5 gal). | jrojas92 |  |  |  | 2015-12-21 14:26 | jrojas92
941 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-09 11:22 | 593 | 122.3 | 9 | 122.3 | [8 empty] | 1.1 | [14 empty] | mrh4 | Not Adjusted |  | 54.1 | 2015-11-24 11:23 | mrh4
942 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-02 14:41 | 515 | 131.8 | 9.2 | [9 empty] | 2 | [13 empty] | ​ST 70 is down to 9 gallons | mrh4 | Not Adjusted |  | 53.1 | 2015-11-02 14:43 | mrh4
943 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-30 15:05 | 462 | 179 | 8.4 |  | 120 | 120 |  | 0.62 | 5.9 | 8.4 | 1.53 | 0.8 | 0.56 |  | 2.27 |  | 897532 | 3170 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 15:08 | jrojas92
944 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-21 09:31 | 423 | 121 | 9.1 | 242 | [8 empty] | 2 | [13 empty] | ​ | mrh4 | Not Adjusted |  | 54.1 | 2015-10-26 09:34 | mrh4
945 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-16 12:00 | 272 | 257.2 | 7.7 | 301 | [8 empty] | 1 | [13 empty] | ​Restarted both cooling towers after cleaning and repairs | mrh4 | Not Adjusted |  | 73.5 | 2015-10-16 12:03 | mrh4
946 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-24 18:39 | 650 | 161 | 8.4 |  | 270 | 214 |  | 0.39 | 5.5 | 10.2 | 0.84 | 0.8 | 0.68 | 0.0684 | 0.51 |  | 897398 | 3114 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-09-30 18:43 | jrojas92
947 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-22 08:50 | 705 | 143.7 | 9.1 | [9 empty] | 0.87 | [14 empty] | mrh4 | Not Adjusted |  |  | 2015-09-22 08:59 | mrh4
948 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-26 16:44 | 659 | 167 | 8.4 |  | 230 | 224 |  | 0.26 | 5.3 | 6.7 | 0.88 | 0.2 | 0.03 | 0.064 | 0.84 |  | 897398 | 2954 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 16:46 | jrojas92
949 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-07-16 13:24 | 714 | 153 | 8.6 |  | 220 | 218 |  | 0 | 5.5 | 8.4 | 0.79 | 0.2 | 4.76 | 0.0722 | 0.59 |  | 895125 | 2294 |  |  |  |  | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-08-18 13:30 | jrojas92
950 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-22 17:34 | 620 | 151 | 8.4 |  | 180 | 186 |  | 0 | 5.1 | 5.3 | 0.82 | 0.2 | 0.02 | 0.127 | 1.22 |  | 897130 | 1824 |  |  |  | Correct | Good | Clean | Clean | Needs Filling | ​Out of ST70 | jrojas92 |  |  |  | 2015-11-14 17:36 | jrojas92
951 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-21 18:24 | 555 | 163 | 8.53 |  | 200 | 172 |  | 0.47 | 3.9 | 7.8 | 0.97 | 0.9 | 1.58 | 0.132 | 0.77 |  | 897130 | 1692 | [7 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:27 | jrojas92
952 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 13:57 | 397 | 127.1 | 8.7 | [9 empty] | 1 | [13 empty] | Fahrenheit​ | mrh4 | Not Adjusted |  | 56.2 | 2015-09-21 13:58 | Jay Dahlstrom
953 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-13 13:33 | 379 | 132.1 | 8.7 | [9 empty] | 0.33 | [13 empty] | ​Fahrenheit | mrh4 | Not Adjusted |  | 55.9 | 2015-09-21 13:34 | Jay Dahlstrom
954 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-04-08 19:01 | 343 | 171 | 7.9 |  | 100 | 98 |  | 0.4 | 4.7 | 0 | 1.81 | 0.6 | 0.47 | 0.0725 | 0.58 |  | 896996 | 1692 | [7 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 19:03 | jrojas92
955 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-06 12:59 | 381 | 139.7 | 8.7 | [9 empty] | 0.37 | [13 empty] | Fahrenheit​ | mrh4 | Not Adjusted |  | 54.2 | 2015-09-21 13:00 | Jay Dahlstrom
956 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-19 12:46 | 392 | 134.4 | 8.7 | [9 empty] | 0.02 | [13 empty] | ​​Fahrenheit | mrh4 | Not Adjusted |  | 54 | 2015-09-21 12:46 | Jay Dahlstrom
957 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-23 09:24 | 265 | 136.5 | 8.5 | [9 empty] | 0.2 | [13 empty] | ​Farhenheit | mrh4 | Not Adjusted |  | 52.2 | 2015-09-21 09:27 | Jay Dahlstrom

## dbo_WaterTreatmentCondenserWate
UniqueID | FacNum | ContentType | LoopType | EntryGroup | SurveyDate | Conductivity | TRASAR | pH | ORP | MAlkalinity | TotalHardness | CalciumHardness | Phosphonate | OrthoPhosphate | Polymer | Zinc | Azole | FreeChlorine | Copper | Iron | TotalBacteria | MakeupMeter | BlowdownMeter | WaterMeterCycles | MildSteelCorrosionRate | MildCopperCorrosionRate | MeteringPumpOperation | UnitCondition | Debris | Filters | ChemicalInventory | Notes | DataEntryUser | PumpSpeedAdjustment | StrokeSetting | Tempurature | Created | CreatedBy
57 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 10:51 | 744 | 127 | 7.9 | [9 empty] | 0.1 |  |  |  |  | 1403 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Free chloirne low as it was not a feed day. | reedhea |  |  |  | 2016-11-09 11:07 | reedhea
58 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-19 14:03 | 750 |  | 9 | 163 | [8 empty] | 0.2 | [13 empty] | ​temp was pretty high. Free Chlorine was going to feed later on that day | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2016-10-24 14:06 | Daimon A. Boccamazzo
59 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-18 12:19 | 746 |  | 8.7 | 148 | [8 empty] | 0.3 | [13 empty] | ​strainer was clean, tower good, no leaks and no alarms | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2016-07-19 12:24 | Daimon A. Boccamazzo
60 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:22 | 734 |  | 8.8 | 177 | [8 empty] | 0.2 | [13 empty] | ​chemicals look good. Probably should order some st70 soon. No leaks on chemical system and the tower looks good no leaks or problems. | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2016-06-02 13:25 | Daimon A. Boccamazzo
61 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-16 22:49 | 725 | 206 | 8.7 |  | 270 | 274 |  | 0.58 | 4.7 | 7.1 | 0.35 | 0.1 | 0.03 | 0.124 | 0.52 |  | 1228.78 | 6937 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 22:53 | jrojas92
62 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-16 13:18 | 741 |  | 8.8 | 392 | [8 empty] | 0.15 | [13 empty] | ​relay 4 pumps every 3rd day at 3pm for 30mins. Relay 5 pumps every 3rd Friday at 10am for 30mins. I'm sure this is the reasoning for the free chlorine level being so low. Need to get the relays named or labeled on the pumps so we know what is what. The s | Daimon A. Boccamazzo | Not Adjusted |  | 85 | 2016-05-16 13:23 | Daimon A. Boccamazzo
63 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 14:27 | [12 empty] | 6.4 | [13 empty] | ​tested the free chlorine level at 2:00pm 5/4/16 and they were 6.4ppm which is above protocol and it stayed in the range for 24 hours. I also turned the blowdown valve back to auto | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 14:30 | Daimon A. Boccamazzo
64 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 09:12 | [12 empty] | 6.8 | [13 empty] | ​need the free chlorine levels to be above 5ppm until 1:50 pm 5/4/16. Pumped st70 into the system for 30 minutes to make sure we stay above 5ppm until testing it at 1:50 pm 5/4/16 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 09:15 | Daimon A. Boccamazzo
65 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-03 13:55 | [12 empty] | 5.3 | [13 empty] | ​pumped st70 into the system for another hour at 1:55pm | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-03 13:56 | Daimon A. Boccamazzo
66 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-03 13:13 | [12 empty] | 4.4 | [13 empty] | ​​4.4 ppm free chlorine at 10:35 am 03MAY16 | dn3 | Not Adjusted |  |  | 2016-05-03 13:16 | dn3
67 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-20 11:49 | [26 empty] | ​fixed connecting tube from porta feed to the pump, for the st70 chemical. Also ran the pump on manual for 5 minutes and there were no leaks | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-20 11:51 | Daimon A. Boccamazzo
68 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-20 08:57 | 746 |  | 7.5 | 260 | [8 empty] | 0.1 | [13 empty] | ​st70 is still offline due to porta feed issues | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-20 08:59 | Daimon A. Boccamazzo
69 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-18 20:44 | 1086 | 153 | 8.7 |  | 420 | 400 |  | 0.42 | 5.4 | 8.1 | 0.31 | 0 | 0.06 | 0.143 | 0.52 |  | 1116.89 | 5958 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Controller was turned off. | jrojas92 |  |  |  | 2016-06-06 20:57 | jrojas92
70 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-28 06:46 | 718 | 162 | 8.5 | 217 | [8 empty] | 0.5 | [14 empty] | Bob A Adams | Not Adjusted |  | 83.5 | 2016-03-29 06:48 | Bob A Adams
71 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-25 21:59 | 730 | 187 | 8.7 |  | 260 | 282 |  | 0.14 | 6 | 9.5 | 0.44 | 0 | 0.11 | 0.134 | 0.47 |  | 1103.49 | 5824 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​​White crust on bottom of ST70 PortaFeed tank basin. | jrojas92 |  |  |  | 2016-04-27 22:10 | jrojas92
72 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 14:09 | 731 | 148 | 8.6 | 210 | [8 empty] | 0.5 | [14 empty] | Bob A Adams | Not Adjusted |  | 87.8 | 2016-03-10 14:11 | Bob A Adams
73 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 11:23 | 739 | 95.7 | 8.4 | 272 | [8 empty] | 0.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 83.6 | 2016-02-08 11:24 | Bob A Adams
74 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-26 14:10 | 746 | 153 | 8.5 | 217 | [8 empty] | 0.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 86 | 2016-01-28 14:11 | Bob A Adams
75 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-12 14:25 | 947 | 152.2 | 8.6 | 153 | [8 empty] | 0.1 | [13 empty] | ​calibrated conductivity | Bob A Adams | Not Adjusted |  | 86 | 2016-01-12 14:27 | Bob A Adams
76 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 14:35 | 558 | 157 | 8.6 | 178 | [8 empty] | 0.4 | [13 empty] | ​chess good. Cond. calibrated | Bob A Adams | Not Adjusted |  | 86 | 2015-12-31 14:41 | Bob A Adams
77 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 13:54 | 725 | 199 | 8.6 |  | 290 | 290 |  | 0 | 5.4 | 10.2 | 0.38 | 0 | 0.03 | 0.1262 | 0.5 |  | 1029.12 | 3200 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-12-21 13:59 | jrojas92
87 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-14 18:00 | 793 | 180 | 8.4 |  | 310 | 280 |  | 0.23 | 3.4 | 4.8 | 0.79 | 0 | 0 | 0.372 | 3.4 |  | 911.2 | [8 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:02 | jrojas92
88 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-04-24 18:40 | 864 | 230 | 8.6 |  | 260 | 340 |  | 0.38 | 5 | 3.8 | 0.62 | 0 | 0 | 0.335 | 4.9 |  | 884.4 | [8 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:43 | jrojas92
89 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-14 13:35 | 732 | 140.2 | 8.7 | [9 empty] | 0.75 | [13 empty] | Fahrenheit​ | mrh4 | Not Adjusted |  | 88.4 | 2015-09-21 13:36 | Jay Dahlstrom
90 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-01 12:51 | 511 | 122.1 | 8.6 | [9 empty] | 0.74 | [13 empty] | ​Fahrenheit​ | mrh4 | Not Adjusted |  | 88.1 | 2015-09-21 12:52 | Jay Dahlstrom
91 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-27 10:16 | 1099 |  |  | 213 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 59 | 2018-10-01 10:16 | RICHARD A. JOHNSON
92 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-22 11:42 | 927 |  |  | 113 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2018-08-30 11:43 | RICHARD A. JOHNSON
93 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 11:05 | 314 | [11 empty] | 0.3 |  |  | 174 | [10 empty] | ​tower is leaking from a water meter valve on the make up water line. A work order has been put in to get the leak fixed. | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2018-08-10 11:07 | Daimon A. Boccamazzo
94 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-12 09:18 | [27 empty] | Jay Dahlstrom | Not Adjusted |  |  | 2018-07-11 09:19 | Jay Dahlstrom
95 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-28 13:15 | 200 |  |  | 157 | [8 empty] | 0 | [13 empty] | ​ | RICHARD A. JOHNSON | Not Adjusted |  | 57 | 2018-06-29 13:17 | RICHARD A. JOHNSON
96 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:11 | 628 |  |  | 226 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-02 10:13 | RICHARD A. JOHNSON
97 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-17 13:26 | [26 empty] | ​couldn't get any water to test tower. System is in winter mode | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-17 13:27 | Daimon A. Boccamazzo
98 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-29 11:51 | 801 |  | 8.9 | 182 | [8 empty] | 0.3 | [13 empty] | ​cleaned strainer. Tower doesn't run too often because there isn't a big demand for it during the winter. | Daimon A. Boccamazzo | Not Adjusted |  | 59 | 2016-11-29 11:55 | Daimon A. Boccamazzo
99 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-06 14:45 | 566 |  | 8.9 | 147 | [8 empty] | 0 | [13 empty] | ​need 5 gallon bucket up there so I can clean the strainer and sensors without getting water everywhere. Also need a 5 gallon bucket of 3dt222 up there | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-09-06 14:48 | Daimon A. Boccamazzo
100 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-02 09:05 | 559 |  | 8.9 | 142 | [8 empty] | 0 | [13 empty] | ​both of the old chemical pumps are leaking. Strainer is good. Feeds keep missing and 3dt222 bucket is empty so need to get some up there | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-08-04 09:08 | Daimon A. Boccamazzo
101 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-30 08:38 | 563 |  | 8.9 | 154 | [8 empty] | 0.1 | [13 empty] | ​chemicals still not hooked up, strainer is cleaned. | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-07-08 08:40 | Daimon A. Boccamazzo
102 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-31 13:04 | 613 |  | 8.2 | 221 | [8 empty] | 0.2 | [13 empty] | ​need to get chemicals hooked up so system can start regular feelings of each chemical when needed. Didn't need to clean the strainer. Changed st70 feed to Monday-Friday at 12 pm for 30 minutes | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-05-31 13:07 | Daimon A. Boccamazzo
103 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 10:36 | 1020 |  | 8.9 | 204 | [8 empty] | 0.01 | [13 empty] | ​old walchem controller, cooling tower controller says "temp err". Orp and ph controller says normal. Still good amount of chemical in both buckets. Need to get a empty bucket up here | Daimon A. Boccamazzo | Not Adjusted |  | 80 | 2016-05-12 10:39 | Daimon A. Boccamazzo
104 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-25 14:11 | [26 empty] | ​tower not running. No load. Ready to run | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-25 14:11 | Daimon A. Boccamazzo
105 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-06 11:53 | 518 | 6 | 8.5 | 284 | [8 empty] | 2 | [13 empty] | ​posca in range. Calibrated temp | Bob A Adams | Not Adjusted |  | 76 | 2016-04-06 11:55 | Bob A Adams
106 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 08:27 | 597 | 8 | 8.5 | 289 | [8 empty] | 0.2 | [13 empty] | ​posca in range. Orp sensor needs to be replaced | Bob A Adams | Not Adjusted |  | 79 | 2016-03-25 08:29 | Bob A Adams
107 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 10:31 | 574 | 6 | 8.4 | 273 | [8 empty] | 0.5 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 72 | 2016-03-10 10:33 | Bob A Adams
108 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 14:05 | 597 | 6 | 7.5 | 305 | [8 empty] | 2 | [14 empty] | Bob A Adams | Not Adjusted |  | 75.5 | 2016-02-08 14:06 | Bob A Adams
109 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-25 13:46 | 652 | 8 | 8.5 | 154 | [8 empty] | 0.2 | [13 empty] | ​Posca in range. Cleaned sensors. | Bob A Adams | Not Adjusted |  | 75 | 2016-01-25 13:47 | Bob A Adams
110 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-06 13:50 | 615 | 8 | 8.5 | 165 | [8 empty] | 0.2 | [13 empty] | ​Posca and free chlorine in range. Cleaned sensors. Calibrated Temp | Bob A Adams | Not Adjusted |  | 76 | 2016-01-06 13:53 | Bob A Adams
111 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 07:21 | 576 | 6 | 8.6 | 390 | [8 empty] | 3.4 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 77 | 2015-12-31 07:24 | Bob A Adams
112 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:57 | 581 | 6 | 8.6 | 299 | [8 empty] | 1.2 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 78 | 2015-12-31 07:59 | Bob A Adams
113 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-01 06:52 | 635 | 8 | 8.6 | 276 | [8 empty] | 0.6 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 73 | 2015-12-04 06:54 | Bob A Adams
114 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-23 14:09 | 599 | 4 | 8.6 | 241 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 74 | 2015-11-30 14:13 | Bob A Adams
115 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-19 06:58 | 602 | 6 | 8.5 | 235 | [8 empty] | 0.6 | [13 empty] | ​cleaned sensors. Posca in range | Bob A Adams | Not Adjusted |  | 71 | 2015-11-20 07:01 | Bob A Adams
116 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-16 14:11 | 622 | 6 | 8.5 | 262 | [8 empty] | 0.6 | [13 empty] | ​Posca in range. Cleaned the sensors | Bob A Adams | Not Adjusted |  | 72 | 2015-11-16 14:13 | Bob A Adams
117 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-09 14:07 | 611 | 6 | 8.6 | 261 | [8 empty] | 0.5 | [13 empty] | ​​Posca in range. Cleaned the sensors | Bob A Adams | Not Adjusted |  | 73 | 2015-11-16 14:11 | Bob A Adams
118 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-05 14:23 | 571 | 6 | 8.4 | 222 | [8 empty] | 0.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 73 | 2015-10-05 14:26 | Bob A Adams
119 | 1104 | 1104-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-15 13:39 | 452 |  | 7.7 | [23 empty] | ​TEI - 3 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 11 | 2015-09-21 13:39 | Jay Dahlstrom
131 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-03-25 11:30 | 660 | 6 | 8.8 | 390 | [8 empty] | 1.7 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 76 | 2016-03-28 11:32 | Bob A Adams
132 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-03-16 11:17 | 628 | 6 | 8.5 | 334 | [8 empty] | 1.3 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 74.8 | 2016-03-16 11:19 | Bob A Adams
133 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-03-11 10:30 | 654 | 5 | 8.6 | 391 | [8 empty] | 1.9 | [13 empty] | ​​posca in range. Replaced bucket of posca | Bob A Adams | Not Adjusted |  | 75.5 | 2016-03-11 10:32 | Bob A Adams
134 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-02-22 13:59 | 643 | 4 | 8.4 | 257 | [8 empty] | 0.8 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 84 | 2016-02-22 14:01 | Bob A Adams
135 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 08:42 | 643 | 5 | 8.5 | 130 | [8 empty] | 0 | [13 empty] | ​Posca in range. Orp and conductivity were out of calibration. | Bob A Adams | Not Adjusted |  | 83.3 | 2016-02-08 08:49 | Bob A Adams
136 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-28 14:23 | 601 | 6 | 8.5 | 292 | [8 empty] | 1.2 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 81 | 2016-01-28 14:24 | Bob A Adams
137 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-15 09:00 | 560 | 6 | 8.5 | 357 | [8 empty] | 2.6 | [13 empty] | ​cleaned orp sensor. Clog in bromine line. Flow meter dirty causing flow meter to stick open. | Bob A Adams | Not Adjusted |  | 84 | 2016-01-15 09:04 | Bob A Adams
138 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 13:06 | 575 | 10 | 8.7 | 180 | [8 empty] | 0.1 | [13 empty] | ​calibrated conductivity & Orp | Bob A Adams | Not Adjusted |  | 75 | 2015-12-31 13:09 | Bob A Adams
139 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-12-08 10:00 | 327 | 8 | 8.1 | 269 | [8 empty] | 0 | [13 empty] | ​CH20 treatment system Primed bromine pump | mrh4 | Not Adjusted |  | 68 | 2015-12-14 10:02 | mrh4
140 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-11-10 11:35 | 634 | 8 | 8.1 | 231 | [8 empty] | 0 | [13 empty] | ​Primed bromine pump CH20 treatment system | mrh4 | Not Adjusted |  | 71.3 | 2015-11-24 11:37 | mrh4
141 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-11-04 14:51 | 571 | 8 | 8.1 | 223 | [8 empty] | 0 | [13 empty] | ​CH20 system Primed bromine pump | mrh4 | Not Adjusted |  | 74.1 | 2015-11-04 14:53 | mrh4
142 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-11-04 09:07 | 571 | 8 | 8.1 | 242 | [8 empty] | 0 | [13 empty] | ​CH20 treatment system Primed bromine pump | mrh4 | Not Adjusted |  | 74.1 | 2015-11-23 09:12 | mrh4
143 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-10-23 09:52 | 563 | 8 | 8.1 | 241 | [8 empty] | 6 | [13 empty] | ​CH20 system. Test results are in their parameters. Reduced ORP set point from 210 to 200 | mrh4 | Not Adjusted |  | 76.1 | 2015-10-26 09:57 | mrh4
144 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-10-15 11:54 | 562 | 8 | 8.1 | 301 | [8 empty] | 0 | [13 empty] | ​Primed bromine pump CH20 system | mrh4 | Not Adjusted |  | 76.1 | 2015-10-16 11:59 | mrh4
145 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-09-23 14:11 | 611 | 8 | 8.1 | [9 empty] | 0 | [13 empty] | ​​ | mrh4 | Up |  |  | 2015-09-23 14:14 | mrh4
146 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-23 14:04 | 611 | 8 | 8.1 | [9 empty] | 0 | [13 empty] | ​​CH2O system Increased bromine pump speed | mrh4 | Not Adjusted |  |  | 2015-09-23 14:11 | mrh4
147 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-17 11:34 | [27 empty] | Bob A Adams | Not Adjusted |  |  | 2015-09-17 11:44 | dn3
148 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-13 13:34 | 581 |  | 8.1 | [23 empty] | ​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 21.6 | 2015-09-21 13:35 | Jay Dahlstrom
149 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-06 13:01 | 588 |  | 8.2 | [23 empty] | TEI - 0 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 22.7 | 2015-09-21 13:02 | Jay Dahlstrom
150 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-01 12:54 | 631 |  | 8.1 | [23 empty] | TEI - 0 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 23.4 | 2015-09-21 12:55 | Jay Dahlstrom
151 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-12 10:42 | 581 |  | 8.5 | [23 empty] | ​​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 23.3 | 2015-09-21 10:42 | Jay Dahlstrom
152 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-03 10:21 | 607 |  | 8.2 | [23 empty] | ​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 21.1 | 2015-09-21 10:22 | Jay Dahlstrom
153 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-25 10:11 | 564 |  | 8.2 | [23 empty] | ​​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 23.7 | 2015-09-21 10:12 | Jay Dahlstrom
154 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-20 09:20 | 606 |  | 8 | [23 empty] | ​TEI - 6 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 25.3 | 2015-09-21 09:20 | Jay Dahlstrom
155 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-20 09:00 | 597 |  | 8.3 | [23 empty] | ​TEI - 0 ppm POSCA - 8 ppm Primed Bromine pump and running flush | mrh4 | Not Adjusted |  | 26.2 | 2015-09-21 09:01 | Jay Dahlstrom
156 | 1111 | 1111-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-15 08:58 | 609 |  | 8.3 | [24 empty] | mrh4 | Not Adjusted |  | 24.4 | 2015-09-21 08:59 | Jay Dahlstrom
157 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:31 | 782 |  |  | 157 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 80 | 2018-08-30 11:32 | RICHARD A. JOHNSON
158 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 11:15 | 795 |  |  | 190 | [8 empty] | 0.3 | [13 empty] | ​two of the chemical pumps are air locked so they need to be changed out. | Daimon A. Boccamazzo | Not Adjusted |  | 83 | 2018-08-10 11:18 | Daimon A. Boccamazzo
159 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-28 13:08 | 271 |  |  | 173 | [8 empty] | 0.4 | [13 empty] | ​ | RICHARD A. JOHNSON | Not Adjusted |  | 77 | 2018-06-29 13:10 | RICHARD A. JOHNSON
160 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-25 13:27 | 798 |  |  | 151 | [8 empty] | 2.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 75 | 2018-04-30 13:28 | RICHARD A. JOHNSON
161 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-20 10:18 | 1077 |  |  | 142 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2018-02-23 10:19 | RICHARD A. JOHNSON
162 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-27 13:50 | 610 |  |  | 226 | [8 empty] | 1.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 77 | 2017-12-29 13:51 | RICHARD A. JOHNSON
163 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-19 10:29 | 102 |  |  | 180 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 75 | 2017-10-23 10:31 | RICHARD A. JOHNSON
164 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:11 | 343 |  |  | 196 | [8 empty] | 1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 79 | 2017-08-24 08:13 | RICHARD A. JOHNSON
165 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 07:41 | 290 |  |  | 157 | [8 empty] | 1.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 79 | 2017-08-02 07:42 | RICHARD A. JOHNSON
166 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-18 13:16 | 105 |  | 9 | 222 | [8 empty] | 0 | [13 empty] | ​started feeding st70 when I was leaving. Tower is constantly draining water cause tower one is constantly running make up water. | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2017-01-25 13:21 | Daimon A. Boccamazzo
167 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-01 13:18 | 80 |  | 9.2 | 184 | [8 empty] | 0.6 | [14 empty] | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-12-01 13:21 | Daimon A. Boccamazzo
168 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-07 10:17 | 223 |  | 9.5 | 175 | [8 empty] | 0.3 | [13 empty] | ​conductivity sensor needs to be calibrated | Daimon A. Boccamazzo | Not Adjusted |  | 77 | 2016-10-14 10:22 | Daimon A. Boccamazzo
169 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-07 07:08 | 203 |  | 8.8 | 152 | [8 empty] | 0.1 | [13 empty] | ​strainer good, conductivity and flow sensors good as well. Conductivity way too low but there are no alarms for it | Daimon A. Boccamazzo | Not Adjusted |  | 81 | 2016-09-08 07:11 | Daimon A. Boccamazzo
170 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-04 10:20 | 432 |  | 8.7 | 167 | [8 empty] | 1.7 | [13 empty] | ​strainer good. Just need to calibrate conductivity sensor cause it is reading 665 and I got 432 | Daimon A. Boccamazzo | Not Adjusted |  | 81 | 2016-08-08 10:23 | Daimon A. Boccamazzo
171 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-28 13:41 | 438 |  | 8.8 | 180 | [8 empty] | 1.5 | [13 empty] | ​need to check calibration on conductivity sensor, it is reading 665 and my meter is reading 438. | Daimon A. Boccamazzo | Not Adjusted |  | 81 | 2016-07-29 13:45 | Daimon A. Boccamazzo
172 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-01 07:53 | 141 |  | 8.7 | 177 | [8 empty] | 0.1 | [13 empty] | ​need chemicals to be hooked up just waiting on Beth to get some time to do that. Strainer is fine. Conductivity sensor needs to be calibrated the controller is reading 410 and my meter is reading 141 | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2016-06-01 07:57 | Daimon A. Boccamazzo
173 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 13:15 | 173 |  | 8.6 | 307 | [8 empty] | 0.04 | [13 empty] | ​cleaned strainer out. Chemicals are here but not hooked up need to get them hooked up asap | Daimon A. Boccamazzo | Not Adjusted |  | 82 | 2016-05-12 13:17 | Daimon A. Boccamazzo
174 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 08:53 | 140 |  | 7.4 | 305 | [8 empty] | 0 | [13 empty] | ​chemicals are here but they are not hooked up yet. Chemical loop strainer is really dirty and needs to be cleaned but I didn't have a bucket to dump the water in. Also there was an alarm for low flow | Daimon A. Boccamazzo | Not Adjusted |  | 80 | 2016-04-29 08:57 | Daimon A. Boccamazzo
175 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-06 13:58 | 165 | 0 | 8.3 | 213 | [8 empty] | 0 | [13 empty] | ​slug fed posca and bromine into cooling tower | Bob A Adams | Not Adjusted |  | 80 | 2016-04-06 14:01 | Bob A Adams
176 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 13:53 | 276 | 0 | 7.8 | 246 | [8 empty] | 0 | [13 empty] | ​Waitng for pump and controller to be programmed | Bob A Adams | Not Adjusted |  | 78 | 2016-03-31 13:58 | Bob A Adams
1 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 10:58 | [26 empty] | ​tower is still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2018-03-16 11:02 | Daimon A. Boccamazzo
2 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 08:49 | [26 empty] | ​tower still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-09-13 08:51 | Daimon A. Boccamazzo
3 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-23 07:29 | [26 empty] | ​tower is still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-26 07:30 | Daimon A. Boccamazzo
4 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-06 10:24 | [26 empty] | ​tower is still offline but has new controller and chemicals ready to go. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-12-12 10:27 | Daimon A. Boccamazzo
5 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-24 14:12 | [26 empty] | ​tower still offline until further notice | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-10-24 14:14 | Daimon A. Boccamazzo
6 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-19 10:24 | [26 empty] | ​tower is still offline, makeup valve shut and drain valve open, tower is dry. New controller and chemicals are there | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-07-20 10:26 | Daimon A. Boccamazzo
7 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:37 | [26 empty] | ​make up water valve is closed and bleed valve is open. Tower is dry. New Nalco controller is hooked up and chemicals are there and ready to be hooked up | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-06-02 13:39 | Daimon A. Boccamazzo
8 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-18 13:10 | [26 empty] | ​chemical are there but not hooked up to the pumps and new Nalco controller is not setup. Closed make up water valve and drained the tower | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-18 13:12 | Daimon A. Boccamazzo
9 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 07:51 | 320 | 0 | 8 | 240 | [8 empty] | 0 | [13 empty] | ​Tower has not been running. | Bob A Adams | Not Adjusted |  | 56.9 | 2016-03-31 07:53 | Bob A Adams
10 | 1294 | 1294-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-02 14:30 | 331 | 8 | 8.1 | 318 | [8 empty] | 2 | [13 empty] | ​This a CH2O treatment system wand the test results are within their parameters | mrh4 | Not Adjusted |  |  | 2015-10-02 14:36 | mrh4
11 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-18 10:20 | 499 |  |  | 82 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 55 | 2018-10-01 10:21 | RICHARD A. JOHNSON
12 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-24 09:21 | 799 |  |  | 134 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2018-07-30 09:22 | RICHARD A. JOHNSON
13 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-18 10:29 | 1077 |  |  | 103 | [8 empty] | 1.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 63 | 2018-05-31 10:29 | RICHARD A. JOHNSON
14 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-26 07:57 | 778 |  |  | 171 | [8 empty] | 4.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 52 | 2018-04-02 07:58 | RICHARD A. JOHNSON
15 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-27 10:51 | 965 |  |  | 202 | [8 empty] | 0.4 | [13 empty] | ​cleaned strainer and flow meter. | Daimon A. Boccamazzo | Not Adjusted |  | 50 | 2018-03-16 10:56 | Daimon A. Boccamazzo
16 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-30 13:23 | 965 |  |  | 136 | [8 empty] | 1.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 51 | 2018-02-01 13:24 | RICHARD A. JOHNSON
17 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-22 12:11 | 740 |  |  | 193 | [8 empty] | 2.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 61 | 2017-12-04 12:13 | RICHARD A. JOHNSON
18 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-30 11:43 | 870 |  |  | 201 | [8 empty] | 1.9 | [13 empty] | ​cleaned strainer and flow meter | Daimon A. Boccamazzo | Not Adjusted |  | 54 | 2017-11-06 11:55 | Daimon A. Boccamazzo
19 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 08:45 | 736 |  |  | 287 | [8 empty] | 0.2 | [13 empty] | ​everything good, cleaned strainer | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2017-09-13 08:48 | Daimon A. Boccamazzo
20 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:26 | 689 |  |  | 266 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-02 10:27 | RICHARD A. JOHNSON
21 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:17 | 684 |  | 9.16 | 212 | [8 empty] | 0.2 | [13 empty] | ​ | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-06-19 07:19 | RICHARD A. JOHNSON
22 | 1108 | 1108-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-04 12:16 | 761 | 94.3 | [10 empty] | 0.08 |  |  |  | 237900 | 314500 |  |  |  | Correct | Good | Dirty | Clean | Level Okay | ​​Not a free Chlorine feed day. Expected low Chlorine concentrations. Cleaned out strainer on controller. | reedhea |  |  |  | 2017-05-04 13:53 | reedhea
23 | 1108 | 1108-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-03-17 11:38 | 601 | 143 | 7.8 | [9 empty] | 0.99 |  |  |  | 2338200 | 311400 | 10 |  |  | Correct | Good | Dirty | Clean | Level Okay | ​​Cleaned strainer, recalibrated conductivity | reedhea |  |  |  | 2017-03-17 11:44 | reedhea
24 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-23 07:25 | [26 empty] | ​tower is offline for the winter | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-26 07:27 | Daimon A. Boccamazzo
25 | 1108 | 1108-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-12-13 13:38 | [16 empty] | 2323600 | 310100 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | reedhea |  |  |  | 2016-12-13 13:51 | reedhea
26 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-06 10:07 | 1060 |  | 8.1 | 100 | [8 empty] | 0 | [13 empty] | ​only a little bit of free chlorine in the tower because the tower is not running as much because it is cold outside so there is no demand for it. So it has no flow which makes the st70 pump miss the fed. | Daimon A. Boccamazzo | Not Adjusted |  | 59 | 2016-12-12 10:14 | Daimon A. Boccamazzo
27 | 1108 | 1108-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 11:11 | 710 | 134 | 7.7 | [9 empty] | 0.03 |  |  |  | 2323600 | 310000 |  |  |  | Correct | Good | Clean | Dirty | Level Okay | ​Sampled 30mins before ST70 biocide feed so free chlorine was expected to be low. Cleaned strainer. No flow. Water meters in gallons. | reedhea |  |  |  | 2016-11-09 11:38 | reedhea
28 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-19 14:06 | 578 |  | 8.9 | 173 | [8 empty] | 0.2 | [13 empty] | ​low free chlorine cause there was no, causing the feed to miss. Tower runs when needed so early in the mornings it won't run cause it's cold out side which means no flow to the controller | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-10-24 14:11 | Daimon A. Boccamazzo
29 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-19 10:19 | 579 |  | 8 | 149 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer. Controller still not working | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-07-20 10:21 | Daimon A. Boccamazzo
30 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:25 | 2029 |  | 8.2 | -75 | [8 empty] | 0.7 | [13 empty] | ​need to get chemicals hooked up asap! Had Rex call Matt from Nalco to manually turn on the bleed valve so the tower would drain some of the bad water out and get some fresh clean water in. | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-06-02 13:29 | Daimon A. Boccamazzo
31 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-18 12:24 | 1963 |  | 8.2 | 230 | [8 empty] | 0.14 | [13 empty] | ​all the chemicals are there and the new Nalco controller is mounted but needs to be set up and hooked up to the chemicals. Strainer will need to be cleaned next time around, need bucket up here. | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-05-18 12:27 | Daimon A. Boccamazzo
32 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-19 09:17 | 634 | 8 | 8.1 | 21168 | [8 empty] | 0 | [13 empty] | ​CH20 system Primed bromine pump | mrh4 | Not Adjusted |  |  | 2015-10-26 09:26 | mrh4
33 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-14 11:48 | 611 | 8 | 8.1 | 211 | [8 empty] | 0 | [13 empty] | ​CH20 system All test results are within parameters | mrh4 | Not Adjusted |  |  | 2015-10-16 11:52 | mrh4
34 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-14 13:36 | 577 |  | 8 | [23 empty] | TEI - 3 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 26.1 | 2015-09-21 13:37 | Jay Dahlstrom
35 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-10 13:02 | 571 |  | 8.1 | [23 empty] | TEI - 0 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 26.2 | 2015-09-21 13:02 | Jay Dahlstrom
36 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-03 12:58 | 581 |  | 8.1 | [23 empty] | TEI - 1 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 28.4 | 2015-09-21 12:58 | Jay Dahlstrom
37 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-19 12:46 | 530 |  | 8.6 | [23 empty] | ​TEI - 3 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 28.3 | 2015-09-21 12:47 | Jay Dahlstrom
38 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-23 09:23 | 551 |  | 8.1 | [23 empty] | ​TEI - 0 ppm POSCA - 8 ppm​ | mrh4 | Up |  | 25.2 | 2015-09-21 09:24 | Jay Dahlstrom
39 | 1108 | 1108-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-11 09:12 | 551 |  | 8.1 | [23 empty] | ​TEI - 0 ppm POSCA - 6 ppm | mrh4 | Not Adjusted |  | 23.7 | 2015-09-21 09:13 | Jay Dahlstrom
40 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-14 10:21 | 881 |  |  | 121 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 86 | 2018-10-01 10:22 | RICHARD A. JOHNSON
41 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-24 09:23 | 876 |  |  | 123 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 86 | 2018-07-30 09:24 | RICHARD A. JOHNSON
42 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-29 10:34 | 871 |  |  | 160 | [8 empty] | 0.5 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 87 | 2018-05-31 10:35 | RICHARD A. JOHNSON
43 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-22 07:48 | 879 |  |  | 148 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 85 | 2018-04-02 07:49 | RICHARD A. JOHNSON
44 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 10:22 | 875 |  |  | 219 | [8 empty] | 0.2 | [13 empty] | ​fed st70 for 30 mins to bring the FC levels up | Daimon A. Boccamazzo | Not Adjusted |  | 85 | 2018-03-16 10:29 | Daimon A. Boccamazzo
45 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-31 13:25 | 866 |  |  | 217 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 83 | 2018-02-01 13:25 | RICHARD A. JOHNSON
46 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-22 12:15 | 718 |  |  | 182 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 88 | 2017-12-04 12:16 | RICHARD A. JOHNSON
47 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 11:17 | 695 |  |  | 301 | [8 empty] | 0.2 | [13 empty] | ​​Changed st70 jug | Daimon A. Boccamazzo | Not Adjusted |  | 87 | 2017-09-11 11:31 | Daimon A. Boccamazzo
48 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:24 | 430 |  |  | 234 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 89 | 2017-08-02 10:25 | RICHARD A. JOHNSON
49 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:23 | 686 |  | 8.88 | 208 | [8 empty] | 2.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 86 | 2017-06-19 07:25 | RICHARD A. JOHNSON
50 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-04 12:15 | 738 | 101 | 8 |  | 90 | [6 empty] | 7 | 0.04 | 0.2 | 0.5 |  | 14.472 | 15223 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​System looks great - no adjustments needed. ​Dropped off the sump pump for transferring ST70 from the portafeed tank to the empty pails. | reedhea |  |  |  | 2017-05-04 13:24 | reedhea
51 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-04-07 10:44 | 816 | 123 | [10 empty] | 0.06 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​​ST70 leaking, free chlorine low. Replacement parts in stock now, working with Daimon to repair | reedhea |  |  |  | 2017-04-07 10:54 | reedhea
52 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-03-17 10:15 | 773 | 117 | 8.6 | [9 empty] | 0.06 |  |  |  | 1420.4 | 14134.4 | 11.9 | 0.4 | 0.02 | Not Correct | Good | Clean | Clean | Level Okay | ​​Date/time changed on trasar. ST70 pump airlocked; pump rerpimed and manually fed for 30 mins. | reedhea |  |  |  | 2017-03-17 10:28 | reedhea
53 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-02-08 14:20 | 725 | 122 | 8.4 | [9 empty] | 0.5 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​​ST70 portafeed leaking into containment basin - Nalco will follwo up | reedhea |  |  |  | 2017-02-08 15:56 | reedhea
54 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-23 07:22 | 742 |  | 8.9 | 240 | [8 empty] | 0.7 | [13 empty] | ​everything is okay. Tower is still running and it is supposed to be shut down during the winter | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2017-01-26 07:25 | Daimon A. Boccamazzo
55 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-12-13 13:33 | 720 | 148 | 8.4 | [9 empty] | 0.1 |  |  |  | 1366.8 | 12176 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Not an ST70 fed day Parameters were within spec. | reedhea |  |  |  | 2016-12-13 13:37 | reedhea
56 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-06 07:55 | 740 |  | 8.9 | 147 | [8 empty] | 1 | [13 empty] | ​everything is all good | Daimon A. Boccamazzo | Not Adjusted |  | 86 | 2016-12-07 07:57 | Daimon A. Boccamazzo
78 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-10 11:38 | 748 | 142 | 8.68 | 0 | [8 empty] | 0 | [13 empty] | ​Slug fed biocide | mrh4 | Not Adjusted |  | 87.9 | 2015-11-24 11:42 | mrh4
79 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-04 14:53 | 747 | 130.1 | 8.7 | 148 | [8 empty] | 1 | [13 empty] | ​ | mrh4 | Not Adjusted |  | 83.7 | 2015-11-04 14:55 | mrh4
80 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-04 09:18 | 747 | 130.1 | 8.7 | [9 empty] | 1 | [14 empty] | mrh4 | Not Adjusted |  | 83.7 | 2015-11-23 09:21 | mrh4
81 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-23 14:26 | 747 | 198 | 8.7 |  | 270 | 304 |  | 0.17 | 4.5 | 10.5 | 0.48 | 0.1 | 0.04 | 0.179 | 0.54 |  | 1005 | 2376 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 14:32 | jrojas92
82 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-28 17:08 | 727 | 193 | 8.6 |  | 260 | 288 |  | 0 | 5.1 | 12.3 | 0.62 | 0.2 | 0.06 | 0.319 | 0.92 |  | 991.6 | 1780 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​First BD meter reading taken because of newly installed meter faceplate. | jrojas92 |  |  |  | 2015-09-30 17:33 | jrojas92
83 | 1008 | 1008-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-23 14:01 | 755 | 130.1 | 9 | [9 empty] | 0.5 | [14 empty] | mrh4 | Not Adjusted |  | 85.5 | 2015-09-23 14:04 | mrh4
84 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-24 16:13 | 727 | 187 | 8.6 |  | 270 | 300 |  | 1.42 | 4.48 | 7 | 0.34 | 0.7 | 0.05 | 0.126 | 0.71 |  | 964.8 |  |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 16:22 | jrojas92
85 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-07-17 11:49 | 755 | 199 | 8.5 |  | 270 | 298 |  | 0.49 | 5.5 | 9.6 | 0.53 | 0.8 | 0.05 | 0.23 | 1.46 |  | 949 | [5 empty] | Good | Clean | Clean | Level Okay | ​Calibrated conductivity meter | jrojas92 |  |  |  | 2015-08-18 12:10 | jrojas92
86 | 1008 | 1008-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-19 17:07 | 168 | 402 | 7.5 |  | 50 | 78 |  | 0.4 | 14.5 | 11.9 | 0.14 | 1.9 | 0.21 | 0.311 | 0.41 |  | 924.6 |  |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 17:12 | jrojas92
120 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-08-31 10:51 | [26 empty] | ​tower is now offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-09-11 10:53 | Daimon A. Boccamazzo
121 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-01-19 14:33 | 750 |  | 8.8 | 268 | [8 empty] | 0.3 | [13 empty] | ​tower will be removed soon | Daimon A. Boccamazzo | Not Adjusted |  | 79 | 2017-01-25 14:38 | Daimon A. Boccamazzo
122 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-12-01 13:29 | 1510 |  | 8.8 | 179 | [8 empty] | 0 | [13 empty] | ​still need to know how to work the controller | Daimon A. Boccamazzo | Not Adjusted |  | 77 | 2016-12-01 13:33 | Daimon A. Boccamazzo
123 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-10-14 13:27 | 662 |  | 8.9 | 166 | [8 empty] | 0.1 | [13 empty] | ​still the old system so I don't know how to use it so I can make adjustments | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-10-24 13:41 | Daimon A. Boccamazzo
124 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-09-08 13:14 | 645 |  | 8.9 | 153 | [8 empty] | 0.1 | [13 empty] | ​still don't know how to work the old walchem controllers. Would like to pump st70 into the system to bring the free chlorine levels up, I always get low readings of st70 | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-09-08 13:16 | Daimon A. Boccamazzo
125 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-08-08 10:38 | 630 |  | 8.9 | 138 | [8 empty] | 0.2 | [13 empty] | ​would like to figure out how to adjust the st70 feeding so I can try and bring the free chlorine levels up a little bit more. | Daimon A. Boccamazzo | Not Adjusted |  | 77 | 2016-08-08 10:45 | Daimon A. Boccamazzo
126 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-07-18 10:26 | 704 |  | 8.9 | 121 | [8 empty] | 0 | [13 empty] | ​changed unibrom plus bucket. Need to know how to use the walchem controllers so I can get the free chlorine levels up | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-07-18 10:29 | Daimon A. Boccamazzo
127 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-06-01 14:57 | 698 |  | 8.9 | 160 | [8 empty] | 0.1 | [13 empty] | ​tower looks good old what hem controller so I can tell when it feeds st70 into the tower. Also found a bucket of the 7341 chemical | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2016-06-01 14:59 | Daimon A. Boccamazzo
128 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-05-16 10:03 | 740 |  | 8.9 | 185 | [8 empty] | 0.23 | [13 empty] | ​system is normal. Probably going to need new bucket of posca next time around. Started pumping posca in the tower after I had taken a sample. Orp/ph controller said output timeout. Still old walchem system | Daimon A. Boccamazzo | Not Adjusted |  | 78 | 2016-05-16 10:08 | Daimon A. Boccamazzo
129 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-04-29 13:13 | 402 |  | 8.7 | 375 | [8 empty] | 0.5 | [13 empty] | ​good flow, still have good amount of chemical in the buckets and there are also extra buckets. Controllers both say normal on them. Also while I let the free chlorine test sit there the water turned more pink and I pressed the green button again to check | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-04-29 13:17 | Daimon A. Boccamazzo
130 | 1111 | 1111-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-04-07 14:28 | 476 | 4 | 8.4 | 292 | [8 empty] | 0.4 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 84 | 2016-04-07 14:29 | Bob A Adams
177 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-05 14:12 | 74 | 0 | 8.6 | 328 | [8 empty] | 1 | [13 empty] | ​towers were not running | Bob A Adams | Not Adjusted |  | 48.4 | 2016-02-05 14:14 | Bob A Adams
178 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-15 14:02 | 170 | 0 | 8.2 | 405 | [8 empty] | 4.2 | [13 empty] | ​Added Bromine the day before. Added Posca just before testing. Pumps were not running | Bob A Adams | Not Adjusted |  | 74 | 2016-01-15 14:05 | Bob A Adams
179 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-24 14:04 | 421 | 8 | 9.28 | [9 empty] | 0.67 | [13 empty] | ​​CH20 controls remain offline until booster pump is installed. Currently manually feeding chemicals at proper levels | mrh4 | Not Adjusted |  | 68.8 | 2015-09-24 14:26 | mrh4
180 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 13:56 | 81 |  | 7.9 | [23 empty] | TEI - 0 ppm POSCA ---​ | mrh4 | Not Adjusted |  | 22.7 | 2015-09-21 13:57 | Jay Dahlstrom
181 | 1194 | 1194-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-17 09:18 | 174 |  | 8.1 | [23 empty] | ​​TEI - o ppm POSCA - 4 ppm | mrh4 | Not Adjusted |  | 11.4 | 2015-09-21 09:19 | Jay Dahlstrom
182 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-20 10:12 | 687 |  |  | 239 | [8 empty] | 6.7 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-10-01 10:13 | RICHARD A. JOHNSON
183 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:33 | 1035 |  |  | 147 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-08-30 11:34 | RICHARD A. JOHNSON
184 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 10:56 | 1348 |  |  | 193 | [8 empty] | 0.1 | [13 empty] | ​still need to get the leak on the top of the tower fixed. Cleaned the water that was on the floor. Tower will feed st70 tomorrow | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2018-08-10 10:59 | Daimon A. Boccamazzo
185 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 06:58 | 1345 |  |  | 248 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-07-03 06:58 | RICHARD A. JOHNSON
186 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-23 13:24 | 1257 |  |  | 261 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2018-04-30 13:25 | RICHARD A. JOHNSON
187 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-22 10:11 | 599 |  |  | 199 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-02-23 10:12 | RICHARD A. JOHNSON
188 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-27 13:56 | 788 |  |  | 302 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2017-12-29 13:57 | RICHARD A. JOHNSON
189 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:23 | 641 |  |  | 208 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2017-08-24 08:24 | RICHARD A. JOHNSON
190 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 07:37 | 589 |  |  | 131 | [8 empty] | 0 | [13 empty] | ​tested on an off day | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-02 07:38 | RICHARD A. JOHNSON
191 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-05 13:16 | 880 |  | 9 | 190 | [8 empty] | 8.8 | [13 empty] | ​tower just fed st70 which is why the free chlorine levels are so high | Daimon A. Boccamazzo | Not Adjusted |  | 64 | 2017-01-17 13:18 | Daimon A. Boccamazzo
192 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-29 11:37 | 1057 |  | 8.5 | 166 | [8 empty] | 0 | [13 empty] | ​adjusted st70 pump from 60 to 80 | Daimon A. Boccamazzo | Up | 80 | 71 | 2016-11-29 11:41 | Daimon A. Boccamazzo
193 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-06 09:13 | 1486 |  | 9.2 | 173 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer and conductivity sensor. Drained water to bring conductivity down and then fed st70. Chemical pumps keep missing their feeds. | Daimon A. Boccamazzo | Not Adjusted |  | 71 | 2016-10-14 09:17 | Daimon A. Boccamazzo
194 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-06 14:39 | 651 |  | 8.9 | 142 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Oxi bio and non oxi bio are still alarming for missed feeds | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-09-06 14:42 | Daimon A. Boccamazzo
195 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-01 11:04 | 556 |  | 8.8 | 127 | [8 empty] | 0.1 | [13 empty] | ​need to find out why the feed times keep missing. Cleaned strainer. Need to check calibration on conductivity sensor cause it is reading 1334 and my meter is reading 556 | Daimon A. Boccamazzo | Not Adjusted |  | 77 | 2016-08-02 11:33 | Daimon A. Boccamazzo
196 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-29 11:58 | [26 empty] | ​tower has no water in it due to plumbers replacing leaking spray pump. Also need to replace conductivity sensor with the right replacement | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-06-29 12:00 | Daimon A. Boccamazzo
197 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-27 11:52 | 2100 |  | 8.9 | 171 | [8 empty] | 0.3 | [13 empty] | ​feed missed for h550 and st70 cause they were both off . I turned them both on and I feed st70 into the system at 80 for 5 mins and set a weekly timer for Monday, Wednesday, and Friday for one hour at 8 o'clock am. Put all pumps at 60 percent and made su | Daimon A. Boccamazzo | Up | 60 | 75 | 2016-05-27 11:58 | Daimon A. Boccamazzo
198 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-10 14:51 | 1242 |  | 8.9 | 237 | [8 empty] | 0.04 | [13 empty] | ​tower is on. Chemicals are there but the pumps are not plugged in. Cleaned out chemical loop strainer | Daimon A. Boccamazzo | Not Adjusted |  | 77 | 2016-05-10 14:53 | Daimon A. Boccamazzo
199 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-22 08:41 | 525 |  | 7.8 | 283 | [8 empty] | 0 | [13 empty] | ​chemicals are there and all full but the system is not plugged in and running yet. Also cleaned out the chemical loop filter | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-22 08:45 | Daimon A. Boccamazzo
407 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-13 11:29 | 618 |  | 8.2 | [23 empty] | ​ORP= 331 TWO= 1.2 OP= 10 | mrh4 | Not Adjusted |  | 55.6 | 2015-09-21 11:30 | Cesar Escobar
408 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-08 11:27 | 591 |  | 8.6 | [23 empty] | ​ORP= 250 TWO= 1.5 OP= 8 | mrh4 | Not Adjusted |  | 56.2 | 2015-09-21 11:29 | Cesar Escobar
409 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-05 11:24 | 536 | [25 empty] | ​​ORP= 270 TWO= .1 OP= 8 | mrh4 | Not Adjusted |  | 60.8 | 2015-09-21 11:26 | Cesar Escobar
410 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-19 10:11 | 1840 |  |  | 218 | [8 empty] | 3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2018-10-01 10:12 | RICHARD A. JOHNSON
411 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:37 | 1806 |  |  | 147 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2018-08-30 11:37 | RICHARD A. JOHNSON
412 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 10:47 | 1610 |  |  | 249 | [8 empty] | 0.7 | [13 empty] | ​tried to let some water run through the chemical loop and clean it out. Also cleaned the strainer and conductivity probe. | Daimon A. Boccamazzo | Not Adjusted |  | 78 | 2018-08-10 10:50 | Daimon A. Boccamazzo
413 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 07:01 | 1394 |  |  | 200 | [8 empty] | 1.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-07-03 07:02 | RICHARD A. JOHNSON
414 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-23 13:22 | 951 |  |  | 161 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 73.5 | 2018-04-30 13:23 | RICHARD A. JOHNSON
415 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-20 10:15 | 325 |  |  | 179 | [8 empty] | 0.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-02-23 10:15 | RICHARD A. JOHNSON
416 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-27 13:55 | 328 |  |  | 206 | [8 empty] | 0.5 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-12-29 13:56 | RICHARD A. JOHNSON
417 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-20 10:43 | 1520 |  |  | 223 | [8 empty] | 0.7 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2017-10-23 10:44 | RICHARD A. JOHNSON
418 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:19 | 679 |  |  | 207 | [8 empty] | 0.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-08-24 08:20 | RICHARD A. JOHNSON
419 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:06 | 626 |  |  | 240 | [8 empty] | 0.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-02 10:08 | RICHARD A. JOHNSON
420 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-05 13:04 | 450 |  | 8.9 | 176 | [8 empty] | 2.6 | [13 empty] | ​​low conductivity due to tower not running as frequently anymore because there is no demand for it in the cold weather | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2017-01-17 13:07 | Daimon A. Boccamazzo
421 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-28 11:16 | 330 |  | 9 | 375 | [8 empty] | 8.8 | [13 empty] | ​free chlorine high because the system had just fed st70 into the tower. Conductivity sensor needs calibration | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-11-29 11:24 | Daimon A. Boccamazzo
422 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-04 09:02 | 210 |  | 9.4 | 180 | [8 empty] | 0.2 | [13 empty] | ​free chlorine low because I tested the tower in between the towers fed cycle. Conductivity sensor needs to be calibrated, it is reading 439 and my meter is reading 210. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-10-14 09:06 | Daimon A. Boccamazzo
423 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-02 14:27 | 554 |  | 8.9 | 200 | [8 empty] | 3.6 | [13 empty] | ​st70 had just feed and that's why chlorine levels are so high, and cleaned strainer | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-09-06 14:30 | Daimon A. Boccamazzo
424 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-26 10:28 | 108 |  | 9.3 | 250 | [8 empty] | 1.5 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Need to check calibration on conductivity sensor, reading at 325 and my meter is reading 108 | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-07-26 10:32 | Daimon A. Boccamazzo
425 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-29 11:47 | 612 |  | 8.8 | 200 | [8 empty] | 4 | [13 empty] | ​cleaned strainer, flow sensor, and conductivity sensor. Changed st70 timer to 1 hour every mon, wed, and fri At 12. Also put a timer on the h-550 for 30 minutes every Sunday at 1. The calibration might need to be checked on the conductivity sensor, it's | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-06-29 11:52 | Daimon A. Boccamazzo
426 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-24 14:48 | 557 |  | 8.8 | 280 | [8 empty] | 4.4 | [13 empty] | ​turned pump speed down to 60. Need to check calibration on conductivity sensor, it is reading 814 and my meter is reading 557. Cleaned strainer. Did visual check on tower as well and it looks good no leaks or problems | Daimon A. Boccamazzo | Down | 60 | 70 | 2016-05-24 15:01 | Daimon A. Boccamazzo
427 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 12:12 | 547 |  | 8.8 | 245 | [8 empty] | 0.42 | [13 empty] | ​check calibration on the controller, it is reading 743 and my conductivity meter is reading 547. I cleaned flow sensor and chemical loop strainer. There is a good amount of chemical in each bucket | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-05-10 12:17 | Daimon A. Boccamazzo
428 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-20 12:20 | 545 |  | 8.3 | 250 | [8 empty] | 7.8 | [13 empty] | ​​tested the tower for free chlorine and it was a pretty high but the best reasoning for that was because I tested it 20 minutes after they cycled through the Chemical, the cycling time is Monday, Wednesday, and Friday at 12. Also cleaned the chemical loo | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-20 12:26 | Daimon A. Boccamazzo
429 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-01 13:59 | 544 | 0 | 8.5 | 781 | [8 empty] | 5 | [13 empty] | ​Controller not programmed. Two chemicals not pumping | Bob A Adams | Not Adjusted |  | 76 | 2016-04-01 14:03 | Bob A Adams
711 | 1150 | 1150-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-10 12:17 | 611 | 101 | 8.2 |  | 70 | 100 | [6 empty] | 0 |  |  |  | 8790.95 |  |  |  |  | Correct | Good | Dirty | Clean | Needs Filling | ​I cleaned out the basket strainer and replaced the ST70 chemical pail. The H550 needs to be replaced. Note: Meter reading is in gallons. | reedhea |  |  |  | 2017-05-10 12:18 | reedhea
712 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-19 13:36 | 551 |  | 9 | 264 | [8 empty] | 0.3 | [13 empty] | ​fixed chemical pumps that were leaking before. And fed st70 for 30 mins to bring the chlorine levels up | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2017-01-25 13:40 | Daimon A. Boccamazzo
713 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-09 13:06 | 2148 |  | 7.9 | 90 | [8 empty] | 0.1 | [13 empty] | ​drained some water out of the system to bring conductivity down. Cleaned strainer, flow and conductivity sensors and opened up two valves connected to a pump that tied into the chemical loop | Daimon A. Boccamazzo | Not Adjusted |  | 63 | 2016-09-12 13:10 | Daimon A. Boccamazzo
714 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-01 14:53 | 690 |  | 8 | 182 | [8 empty] | 0.1 | [13 empty] | ​new Nalco controller but still using ch2o chemical. Need to order Nalco chemicals jugs for the system and hook them up. Tower is good. Strainer will need to be cleaned next time around. | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-06-01 14:55 | Daimon A. Boccamazzo
715 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-13 07:24 | 681 |  | 8.7 | 242 | [8 empty] | 1.2 | [13 empty] | ​new Nalco controller hooked up. Chemicals are not here yet, strainer is okay | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2016-05-16 07:27 | Daimon A. Boccamazzo
716 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 13:08 | 715 |  | 8.6 | 410 | [8 empty] | 8.8 | [13 empty] | ​old walchem controllers, don't know how to use it to check it and see when the system pumped st70 into it. Still good amount of chemical in the buckets. Also controllers said normal on both of them. | Daimon A. Boccamazzo | Not Adjusted |  | 63 | 2016-04-29 13:12 | Daimon A. Boccamazzo
717 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-07 14:23 | 750 | 6 | 8.3 | 285 | [8 empty] | 0.5 | [13 empty] | Posca in range ​ | Bob A Adams | Not Adjusted |  | 66 | 2016-04-07 14:27 | Bob A Adams
718 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 06:35 | 745 | 9 | 8.4 | 213 | [8 empty] | 0.5 | [13 empty] | Posca in range ​ | Bob A Adams | Not Adjusted |  | 63 | 2016-03-29 06:37 | Bob A Adams
719 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-11 14:04 | 455 | 4 | 8.5 | 262 | [8 empty] | 0.4 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 63 | 2016-03-11 14:06 | Bob A Adams
720 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-22 14:14 | 487 | 6 | 8.4 | 253 | [8 empty] | 0.5 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 64 | 2016-02-22 14:16 | Bob A Adams
721 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 11:19 | 558 | 6 | 8.4 | 293 | [8 empty] | 0.4 | [13 empty] | ​free chlorine in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 67 | 2016-02-08 11:22 | Bob A Adams
722 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-28 14:19 | 610 | 8 | 8.5 | 252 | [8 empty] | 0.6 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 64 | 2016-01-28 14:21 | Bob A Adams
723 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-14 10:46 | 918 | 10 | 8.6 | 267 | [8 empty] | 0.2 | [13 empty] | ​Posca and free chlorine in range. Cleaned sensors. Calibrated conductivity and orp. Conductivity sensor failed. Replaced conductivity sensor. | Bob A Adams | Not Adjusted |  | 68 | 2016-01-14 10:49 | Bob A Adams
724 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 13:02 | 760 | 12 | 8.6 | 164 | [8 empty] | 0 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 63 | 2015-12-31 13:05 | Bob A Adams
725 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 09:55 | 621 | 8 | 8.1 | 221 | [8 empty] | 0 | [13 empty] | ​CH20 treatment system Primed bromine pump | mrh4 | Not Adjusted |  | 71 | 2015-12-14 09:58 | mrh4
726 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-09 11:28 | 567 | 8 | 8 | 210 | [8 empty] | 0 | [14 empty] | mrh4 | Not Adjusted |  | 66.3 | 2015-11-24 11:30 | mrh4
727 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-04 14:47 | 551 | 8 | 8.1 | 221 | [8 empty] | 0 | [13 empty] | ​CH20 system Primed bromine pump | mrh4 | Not Adjusted |  | 67.1 | 2015-11-04 14:51 | mrh4
728 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-04 08:57 | 551 | 8 | 8 | 221 | [8 empty] | 0 | [13 empty] | ​CH20 tower Primed bromine pump | mrh4 | Not Adjusted |  | 67.1 | 2015-11-23 09:04 | mrh4
729 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-23 09:44 | 614 | 8 | 8.1 | 221 | [8 empty] | 4 | [13 empty] | ​CH20 system. Test results are within their parameters Reduced bromine pump speed | mrh4 | Not Adjusted |  | 71.1 | 2015-10-26 09:49 | mrh4
730 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-01 14:03 | 352 | 8 | 8.1 | [9 empty] | 0 | [13 empty] | ​ ​Ch2O System C/T has slow leak in drain line. Due to a possible clogged drain C/T drains to parking lot | mrh4 | Up |  |  | 2015-10-01 14:09 | mrh4
731 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-22 14:52 | 426 | 8 | 7.85 | [9 empty] | 0 | [13 empty] | ​This is a Ch2O system and is within recommended parameters except for FC Bromine pump needed to be primed and is now at 3 ppm | mrh4 | Not Adjusted |  |  | 2015-09-22 14:57 | mrh4
732 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 13:58 | 591 |  | 8.1 | [23 empty] | ​​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.9 | 2015-09-21 13:58 | Jay Dahlstrom
733 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-13 13:34 | 607 |  | 8 | [23 empty] | TEI - 3 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 18.4 | 2015-09-21 13:34 | Jay Dahlstrom
200 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-04 12:51 | 714 | 0 | 8.4 | 175 | [8 empty] | 0 | [13 empty] | ​waiting on the the Nalco controller to be programmed and chemicals hooked up. | Bob A Adams | Not Adjusted |  | 76 | 2016-04-04 12:54 | Bob A Adams
201 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-28 06:41 | 492 | 0 | 8.6 | 209 | [8 empty] | 0 | [13 empty] | ​​waiting for chemical system to be started up. | Bob A Adams | Not Adjusted |  |  | 2016-03-29 06:46 | Bob A Adams
202 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-07 08:55 | 768 | 4 | 8.6 | 339 | [8 empty] | 0 | [14 empty] | Bob A Adams | Not Adjusted |  | 68.5 | 2016-03-07 08:56 | Bob A Adams
203 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-11 08:26 | 788 | 0 | 8.5 | 152 | [8 empty] | 0 | [13 empty] | ​put chemical in feeder | Bob A Adams | Not Adjusted |  | 70 | 2016-02-12 08:31 | Bob A Adams
204 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-06 13:46 | 816 | 2 | 8.7 | 194 | [8 empty] | 0.1 | [13 empty] | ​ | Bob A Adams | Not Adjusted |  | 73 | 2016-01-06 13:48 | Bob A Adams
205 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:48 | 810 | 2 | 8.7 | 300 | [8 empty] | 0.6 | [13 empty] | ​ | Bob A Adams | Not Adjusted |  | 71 | 2015-12-31 07:50 | Bob A Adams
206 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-11 07:18 | 804 | 2 | 8.6 | 226 | [8 empty] | 0 | [13 empty] | ​ | Bob A Adams | Not Adjusted |  | 74 | 2015-12-31 07:21 | Bob A Adams
207 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-11 07:05 | 515 | 4 | 8.4 | 244 | [8 empty] | 0 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 72 | 2015-12-31 07:10 | Bob A Adams
208 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-06 14:38 | 617 | 4 | 8.6 | 600 | [8 empty] | 8.8 | [14 empty] | Bob A Adams | Not Adjusted |  | 75.2 | 2015-11-06 14:39 | Bob A Adams
209 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-28 06:58 | 2864 | 0 | 8.8 | 260 | [8 empty] | 0 | [13 empty] | ​calibrated conductivity | Bob A Adams | Not Adjusted |  | 74.3 | 2015-11-03 07:01 | Bob A Adams
210 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-05 13:32 | 689 |  | 8.6 | [23 empty] | ​ORP - 300 TWO - .7 OP - 4 | mrh4 | Not Adjusted |  | 73.2 | 2015-09-22 13:33 | Jay Dahlstrom
211 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-28 13:31 | 755 |  | 8.6 | [23 empty] | ​​ORP - 675 TWO - Too High OP - 24 | mrh4 | Not Adjusted |  | 73 | 2015-09-22 13:31 | Jay Dahlstrom
212 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 13:30 | 702 |  | 8.7 | [23 empty] | ​ORP - 450 TWO - 1.1 OP - .2 | mrh4 | Not Adjusted |  | 72 | 2015-09-22 13:31 | Jay Dahlstrom
213 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-15 13:41 | 631 |  | 8 | [23 empty] | ​TEI - 20+ ppm POSCA - 20+ ppm | mrh4 | Not Adjusted |  | 24.3 | 2015-09-21 13:41 | Jay Dahlstrom
214 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-04 13:29 | 679 |  | 8.5 | [23 empty] | ​ORP - 610 TWO - 4.2 OP - Too high | mrh4 | Not Adjusted |  | 72 | 2015-09-22 13:30 | Jay Dahlstrom
215 | 1324 | 1324-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-05 13:23 | 751 |  | 8.6 | [23 empty] | ​ORP - 560 TWO - 4.5 OP - 24 | mrh4 | Not Adjusted |  | 70.1 | 2015-09-22 13:28 | Jay Dahlstrom
216 | 1153 | 1153-Ccondenser_Water-NALCO | Condenser Water | NALCO | 2015-09-29 18:51 | 449 | 166 | 8.3 |  | 120 | 102 |  | 0 | 4.1 | 7.9 | 2.3 | 0.8 | 0.01 | 0.1201 | 0.59 |  | 8339 | 5730 |  |  |  |  | Good | Clean |  | Needs Filling | ​Chemical tubing is broken and cracked from exposure to the sun/heat. ST70 bucket is nearly empty. | jrojas92 |  |  |  | 2015-09-30 18:58 | jrojas92
217 | 1153 | 1153-Ccondenser_Water-NALCO | Condenser Water | NALCO | 2015-07-16 13:36 | 2543 | 286 | 8 |  | 280 | 100 |  | 0.46 | 10.7 | 12.2 | 4.7 | 0.6 | 13.9 | 0.248 | 0.97 |  | 8056 | 5730 | [5 empty] | Clean |  | Needs Filling | ​​Cooling tower was not running, and there was no flow through the injection quill (flow switch). The controller had low conductivity alarm because there was no flow through the probe. Low on ST-70 inventory. | jrojas92 |  |  |  | 2015-08-18 13:49 | jrojas92
218 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-14 10:24 | 864 |  |  | 145 | [8 empty] | 8.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 59 | 2018-10-01 10:25 | RICHARD A. JOHNSON
219 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-26 09:27 | 608 |  |  | 182 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-07-30 09:27 | RICHARD A. JOHNSON
220 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 08:54 | 260 |  |  | 175 | [8 empty] | 0.6 | [13 empty] | ​fed st70 for 30mins at 100% tower is still on stand by. | Daimon A. Boccamazzo | Not Adjusted |  | 48 | 2018-03-16 09:08 | Daimon A. Boccamazzo
221 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 11:11 | [26 empty] | ​could not get a sample. Spray pump needs to be replaced | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-09-11 11:12 | Daimon A. Boccamazzo
222 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:07 | 1050 |  | 9.22 | 183 | [8 empty] | 7.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 60 | 2017-06-19 07:09 | RICHARD A. JOHNSON
223 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-04 12:51 | 259 | 111.75 | [10 empty] | 0 | [8 empty] | Correct | Good | Dirty |  | Needs Filling | ​​There was no flow through the system due to bio growth restricting flow. The system was cleaned of debri and flow restoredd. The conductivty was low due to continued overflow. The blowdown solenoid was verified to be working properly so the overflow is | reedhea |  |  |  | 2017-05-04 12:56 | reedhea
224 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-03-31 10:18 | 230 | 102 | 7.3 | [9 empty] | 0 |  |  |  | 3057.3 | 100.54 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Conductivity low. Drain still leaking. | reedhea |  |  |  | 2017-03-31 10:20 | reedhea
225 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-02-08 10:33 | 244 | 122 | 7.6 | [9 empty] | 0.2 |  |  |  | 26667 | 100.54 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​MU meter in Cuft. BD darin leaking. Possible overflow or leaking solenoid | reedhea |  |  |  | 2017-02-08 10:37 | reedhea
226 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-20 07:16 | 320 |  | 9.3 | 250 | [8 empty] | 0 | [13 empty] | ​scheduled to feed st70 at 4pm. Tower is still on hand until needed | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2017-01-26 07:19 | Daimon A. Boccamazzo
227 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-12-13 13:12 | 205 | 108 | 7.5 | [9 empty] | 0.11 |  |  |  | 1987 | 100.54 |  |  |  | Correct | Good | Clean | Clean | Needs Filling | ​​MU METER IN CU FT. ST70 PAIL EMPTY CONDUCTIVITY RECALIBRATED | reedhea |  |  |  | 2016-12-13 13:17 | reedhea
228 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-05 07:48 | 226 |  | 10.3 | 137 | [8 empty] | 0.3 | [13 empty] | ​tower still on stand by | Daimon A. Boccamazzo | Not Adjusted |  | 42 | 2016-12-07 07:51 | Daimon A. Boccamazzo
229 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 10:35 | 705 | 110 | 7.7 | [9 empty] | 0.53 |  |  |  | 1780 | 100.54 | 17 |  |  | Correct | Good | Clean | Clean | Level Okay | ​Make-up meter is in cu ft not gallons. Two point calibration completed on controller conductivity. | reedhea |  |  |  | 2016-11-09 10:38 | reedhea
230 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-18 13:48 | 600 |  | 9.4 | 200 | [8 empty] | 8.8 | [13 empty] | ​strainer goo but conductivity probe needs calibration. Also there was an alarm saying relay 7 timed out but not sure what relay 7 is for | Daimon A. Boccamazzo | Not Adjusted |  | 50 | 2016-10-24 13:52 | Daimon A. Boccamazzo
231 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-08 13:19 | 251 |  | 8.8 | 165 | [8 empty] | 0.1 | [13 empty] | ​plugged in controller, it just needs to be programmed now. Cleaned strainer. Also the pumps need to be hard wired in to the controller. I plugged in the st70 pump into another outlet and pumped some into the system at 100% for about tens minutes and brou | Daimon A. Boccamazzo | Not Adjusted |  | 60 | 2016-09-08 13:24 | Daimon A. Boccamazzo
232 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-18 10:32 | 256 |  | 8.7 | 145 | [8 empty] | 0.1 | [13 empty] | ​need to figure out if the tower needs to be drained or not cause it is hardly used. New controller is there but not plugged in | Daimon A. Boccamazzo | Not Adjusted |  | 56 | 2016-07-18 10:35 | Daimon A. Boccamazzo
233 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:15 | 364 |  | 8.6 | 175 | [8 empty] | 0 | [13 empty] | ​tower is still off line until needed. Chemicals are full and there is an extra h-550 and st70 bucket up there as well. | Daimon A. Boccamazzo | Not Adjusted |  | 63 | 2016-06-02 13:18 | Daimon A. Boccamazzo
234 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-22 23:35 | 345 | 0 | 7.8 |  | 80 | 64 |  |  | 0 | 0 | 1.49 | 0 | 0 | 0.146 | 0.71 |  | 126 | 100 |  |  |  | Correct |  |  |  | Level Okay | Tower & controller were off. | jrojas92 |  |  |  | 2016-06-06 23:39 | jrojas92
235 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-18 12:20 | 397 |  | 8.5 | 285 | [8 empty] | 0.06 | [13 empty] | ​old walchem controller but new Nalco pumps. Tower is on but still not running. Controller for the chemical feed is not turned on | Daimon A. Boccamazzo | Not Adjusted |  | 56 | 2016-05-18 12:23 | Daimon A. Boccamazzo
236 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-29 22:08 | 352 | 0 | 8 |  | 60 | 52 |  | 0.12 | 0.3 | 0 | 1.26 | 0.1 | 1.02 | 0.135 | 0.67 |  | 113 | 100 |  |  |  | Correct |  |  |  | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 22:12 | jrojas92
237 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 07:24 | [26 empty] | cooling tower is off, all chemicals are full plus there are extra chemicals there as well. Also I changed the speed to 60 on both the st70 and the h-550 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-02 07:27 | Daimon A. Boccamazzo
238 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-08 14:10 | 361 | 250 | 8.5 | 400 | [8 empty] | 8.5 | [13 empty] | ​bled system for 10 minutes | Bob A Adams | Not Adjusted |  | 61 | 2016-04-08 14:12 | Bob A Adams
239 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-25 20:04 | 523 | 0 | 10.1 |  | 40 | 30 |  | 0 | 0.3 | 0 | 0.16 | 0.1 | 81 | 0.067 | 0.14 |  | 53 | 89 | [7 empty] | Level Okay | ​Tower was BD for ~10min because high free Cl. Tower & controller off. | jrojas92 |  |  |  | 2016-06-06 20:08 | jrojas92
240 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 06:28 | 610 | 250 | 10.1 | 500 | [8 empty] | 8.8 | [13 empty] | ​Chemical system continues to pump when cooling tower is not running. Drained water to lower chemical level. | Bob A Adams | Not Adjusted |  | 51 | 2016-03-29 06:34 | Bob A Adams
241 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-22 13:20 | 1633 | 200 | 10 | 303 | [8 empty] | 8.8 | [13 empty] | ​controller kept feeding chemical when tower was not running. Turned off controller until I can program not to pump with no flow. Drained half water and filled. | Bob A Adams | Not Adjusted | 49.7 |  | 2016-02-22 13:24 | Bob A Adams
242 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-12 14:26 | 4424 | 250 | 11.1 | 380 | [8 empty] | 3.5 | [13 empty] | ​Drained tower water and filled back up. Trasar was reading Hi Conc. | Bob A Adams | Not Adjusted |  | 54.6 | 2016-02-12 14:31 | Bob A Adams
243 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-05 14:19 | 2818 | 250 | 9.8 | 300 | [8 empty] | 9.8 | [13 empty] | ​Trasar reading said "Hi". Had to turn tower on hand to get water flowing | Bob A Adams | Not Adjusted |  | 49.7 | 2016-02-05 14:22 | Bob A Adams
244 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 13:47 | 289 | 6.2 | 8.4 |  | 120 | 122 |  | 0.26 | 0.6 | 0 | 0.39 | 0.4 | 0 | 0.0447 | 0.05 |  | 8800 | 5736 | [5 empty] | Clean |  |  | Needs more ST70 chemical (<1/2 gal). | jrojas92 |  |  |  | 2015-12-22 13:55 | jrojas92
245 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-29 15:12 | 416 | 118 | 8.3 |  | 120 | 116 |  | 0.82 | 3.3 | 5.5 | 1.87 | 0.7 | 0.01 | 0.114 | 0.41 |  | 8373 | 5736 | [7 empty] | Needs Filling | ​Needs more ST70 chemical. | jrojas92 |  |  |  | 2015-11-14 15:16 | jrojas92
246 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-26 16:49 | 1612 | 309 | 8.2 |  | 170 | 78 |  | 0 | 9.6 |  | 4.26 | 1.2 | 0 | 0.205 | 1.3 |  | 8115 | 5730 | [8 empty] | ​Chem tubing is cracked/broken | jrojas92 |  |  |  | 2015-11-14 16:52 | jrojas92
247 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-19 17:40 | 3642 | 322 | 8.9 |  | 320 | 98 |  | 0.06 | 11.9 | 10.9 | 5.56 | 1.1 | 0.16 | 0.225 | 0.56 |  | 7965 | 5720 | [9 empty] | jrojas92 |  |  |  | 2015-11-14 17:42 | jrojas92
248 | 1153 | 1153-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-28 18:30 | 2032 | 305 | 8 |  | 200 | 94 |  | 1.46 | 11.9 | 11.4 | 5.02 | 0.4 | 0.02 | 0.195 | 0.39 |  | 7905 | 5710 | [7 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:32 | jrojas92
249 | 1153 | 1153-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-20 08:54 | 577 |  | 7 | [9 empty] | 0.23 | [13 empty] | ​POSCA --- | mrh4 | Not Adjusted |  | 22.4 | 2015-09-22 08:55 | Jay Dahlstrom
250 | 1119 | 1119-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-06 11:55 | [26 empty] | ​tower is closed down. Water, power, chemicals turned off | Bob A Adams | Not Adjusted |  |  | 2016-04-06 11:56 | Bob A Adams
251 | 1119 | 1119-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 08:30 | 0 | 0 | 0 | 0 | [8 empty] | 0 | [13 empty] | ​Towers are drained and turned off of chemicals and power | Bob A Adams | Not Adjusted |  | 0 | 2016-03-25 08:31 | Bob A Adams
252 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-17 10:22 | 1570 |  |  | 143 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-10-01 10:23 | RICHARD A. JOHNSON
253 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-27 09:20 | 1006 |  |  | 185 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-07-30 09:21 | RICHARD A. JOHNSON
254 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-29 10:35 | 469 |  |  | 148 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2018-05-31 10:36 | RICHARD A. JOHNSON
255 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-26 07:56 | 160 |  |  | 169 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-04-02 07:57 | RICHARD A. JOHNSON
256 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-27 11:04 | 72 |  |  | 189 | [8 empty] | 0.1 | [13 empty] | ​tower is still making up water. Trying to get it fixed | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2018-03-16 11:23 | Daimon A. Boccamazzo
257 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-30 13:21 | 84 |  |  | 202 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-02-01 13:22 | RICHARD A. JOHNSON
258 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-21 12:08 | 124 |  |  | 161 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-12-04 12:10 | RICHARD A. JOHNSON
259 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-30 08:22 | 80 |  |  | 196 | [8 empty] | 0.8 | [13 empty] | ​manually closed make up water valve so it would stop over flowing the tower until I can fix the solenoid valve | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2017-11-06 08:36 | Daimon A. Boccamazzo
260 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 08:52 | 147 |  |  | 265 | [8 empty] | 0.2 | [13 empty] | ​st70 will feed tomorrow. FC reading good for an off day | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2017-09-13 08:58 | Daimon A. Boccamazzo
261 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:22 | 3096 |  | 8.61 | 183 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 61 | 2017-06-19 07:23 | RICHARD A. JOHNSON
262 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-10 13:27 | 2750 | 130 | 8.9 | [9 empty] | 0 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​​Chemistry looks good - conductivity is high. Troubleshooting blowdown solenoid. | reedhea |  |  |  | 2017-05-10 13:28 | reedhea
263 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-23 07:32 | 2236 |  | 8.7 | 266 | [8 empty] | 0.1 | [13 empty] | ​will feed st70 at 2pm for 1hr. Not too worried about the low FC levels cause it doesn't feed over the weekend. | Daimon A. Boccamazzo | Not Adjusted |  | 51 | 2017-01-26 07:35 | Daimon A. Boccamazzo
264 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-12-13 14:18 | 2542 | 111 | 8.4 | [9 empty] | 0.12 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​Conductivity is high - | reedhea |  |  |  | 2016-12-13 14:22 | reedhea
265 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-06 10:15 | 2580 |  | 8.7 | 150 | [8 empty] | 0.6 | [13 empty] | ​need to get the tower clean so the conductivity will go down | Daimon A. Boccamazzo | Not Adjusted |  | 63 | 2016-12-12 10:17 | Daimon A. Boccamazzo
266 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 13:05 | 2482 | 163 | 8.3 | [9 empty] | 0 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​System was in blowdown lock-out mode. I manually set the controller to blowdown for 30mins to decrease conductivity. | reedhea |  |  |  | 2016-11-09 13:29 | reedhea
267 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-20 14:17 | 2980 |  | 9 | 173 | [8 empty] | 0.3 | [13 empty] | ​can't get conductivity to go down, even when I drain water out of the system it barley moves the number down | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-10-24 14:25 | Daimon A. Boccamazzo
268 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-19 10:21 | 1613 |  | 8.7 | 139 | [8 empty] | 1.1 | [13 empty] | ​cleaned tower, changed side stream filter, and everything else is good | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2016-07-20 10:24 | Daimon A. Boccamazzo
269 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:30 | 641 |  | 8.8 | 115 | [8 empty] | 0.1 | [13 empty] | ​strainer is clean. Tower looks good, no problems or leaks | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-06-02 13:34 | Daimon A. Boccamazzo
270 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-16 23:00 | 708 | 183 | 8.6 |  | 250 | 286 |  | 0.69 | 4.4 | 4.7 | 0.14 | 0 | 0 | 0.125 | 0.14 |  | 1416570 | 170580 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 23:03 | jrojas92
271 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-16 13:13 | 725 |  | 8.77 | 243 | [8 empty] | 0.52 | [13 empty] | ​all systems good strainer didn't need to cleaned, no leaks or problems | Daimon A. Boccamazzo | Not Adjusted |  | 61 | 2016-05-18 13:15 | Daimon A. Boccamazzo
272 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-28 14:11 | 734 |  | 8 | 294 | [8 empty] | 0.1 | [13 empty] | ​changed copper corrosion sensor, loosened chemical loop filter. Also changed the trasar chemical pump and fixed the h550 leak and also primed both of those Chicanos after fixing the problems that they had | Daimon A. Boccamazzo | Not Adjusted |  | 61 | 2016-04-28 14:14 | Daimon A. Boccamazzo
273 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-26 21:04 | 702 | 165 | 8.6 |  | 230 | 262 |  | 0.83 | 4.4 | 5.8 | 0.14 | 0.1 | 0 | 0.147 | 0.81 |  | 1404470 | 169560 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 21:08 | jrojas92
274 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-26 15:06 | [26 empty] | ​water treatment loop off due to leaky copper corrosion probe, found all chem. pumps @ 100% (adjusted all to 60%), opened H-550 portafeed valve to inlet of pump, 2DT222 pump leaks, can't remove screen housing on treatment loop (too tight will use strap wr | dn3 | Not Adjusted |  |  | 2016-04-26 15:08 | dn3
275 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 07:23 | 677 | 166.6 | 8.2 | 205 | [8 empty] | 0.2 | [13 empty] | ​Turned on st70 for 10 min. Calibrated orp | Bob A Adams | Not Adjusted |  | 66 | 2016-03-31 07:26 | Bob A Adams
276 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-25 22:18 | 669 | 167 | 8.4 |  | 140 | 184 |  | 0.51 | 3.4 | 3.2 | 0.14 | 0 | 0.15 | 0.12 | 0.27 |  | 1392260 | 168170 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-04-27 22:26 | jrojas92
277 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-11 11:04 | 721 | 116 | 8.5 | 325 | [8 empty] | 1.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 68.1 | 2016-03-11 11:05 | Bob A Adams
278 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 14:07 | 905 | 139 | 8.3 | 220 | [8 empty] | 0 | [14 empty] | Bob A Adams | Not Adjusted |  | 62 | 2016-03-10 14:09 | Bob A Adams
279 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-05 14:14 | 691 | 99 | 8.2 | 231 | [8 empty] | 0 | [13 empty] | ​stabrex line was broken and leaking all over floor | Bob A Adams | Not Adjusted |  | 65 | 2016-02-05 14:16 | Bob A Adams
280 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 13:10 | 702 | 195.8 | 8.5 | 182 | [8 empty] | 9 | [14 empty] | Bob A Adams | Not Adjusted |  | 65 | 2015-12-31 13:14 | Bob A Adams
281 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-30 14:04 | 673 | 198 | 8.4 |  | 250 | 304 |  | 0 | 4.5 | 7.4 | 0.19 | 0 | 0.01 | 0.0892 | 0.1 |  | 1378838 | 167244 |  |  |  |  | Good | Clean | Clean | Level Okay | ​Should check ST70 pump operation, its not feeding chemical. | jrojas92 |  |  |  | 2015-12-21 14:08 | jrojas92
282 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-05 11:09 | 685 | 150.6 | 8.6 | 142 | [8 empty] | 1.9 | [13 empty] | ​ | mrh4 | Not Adjusted |  | 67.7 | 2015-11-24 11:11 | mrh4
283 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-23 14:36 | 682 | 208 | 8.6 |  | 280 | 316 |  | 0.39 | 4.8 | 9.4 | 0.13 | 0.1 | 0.02 | 0.067 | 0.06 |  | 1374110 | 166810 |  |  |  |  | Good | Clean | Clean | Level Okay | ST70 still not feeding (clogged). | jrojas92 |  |  |  | 2015-11-14 14:42 | jrojas92
284 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-23 09:59 | 691 | 147.1 | 9.3 | 131 | [8 empty] | 0 | [13 empty] | ​slug fed biocides Changed side stream filter | mrh4 | Not Adjusted |  | 68.8 | 2015-10-26 10:02 | mrh4
285 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-28 17:47 | 682 | 218 | 8.5 |  | 250 | 310 |  | 0 | 5.7 | 10.3 | 0.13 | 0 | 0.04 | 0.0526 | 0.16 |  | 1365870 | 166050 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​ST70 still appears to be clogged. Performed draw-test, but was not feeding and suction side tubing was clear/empty. | jrojas92 |  |  |  | 2015-09-30 18:07 | jrojas92
286 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-24 16:26 | 667 | 193 | 8.6 |  | 250 | 292 |  | 0.35 | 5.04 | 6.6 | 0.22 | 0.1 | 0.02 | 0.0859 | 0.82 |  | 1347950 | 164620 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​ST70 not feeding (clogged) | jrojas92 |  |  |  | 2015-11-14 16:29 | jrojas92
287 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-07-17 12:24 | 661 | 185 | 8.6 |  | 260 | 300 |  | 0.33 | 4.8 | 7.7 | 0.17 | 0 | 0 | 0.0956 | 0.34 |  | 1318700 | 162430 |  |  |  |  | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-08-18 12:40 | jrojas92
288 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-19 17:16 | 247 | 186 | 7.8 |  | 80 | 108 |  | 0 | 7 | 9.2 | 0.12 | 0.6 | 0.01 | 0.119 | 1.02 |  | 1287220 | 161220 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 17:19 | jrojas92
289 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-14 18:08 | 707 | 199 | 8.2 |  | 300 | 300 |  | 0.65 | 4.6 | 7 | 0.12 | 0.5 | 0.13 | 0.246 | 0.94 |  | 1268160 | 159760 | [7 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:11 | jrojas92
290 | 1200 | 1200-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-04-24 18:47 | 692 | 224 | 8.1 |  | 230 | 314 |  | 1.34 | 5 | 10.2 | 0.28 | 0 | 0.03 | 0.292 | 0.14 | [10 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:50 | jrojas92
291 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-14 13:37 | 681 | 155.5 | 8.9 | [23 empty] | Fahrenheit​ | mrh4 | Not Adjusted |  | 54.6 | 2015-09-21 13:38 | Jay Dahlstrom
292 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-27 10:16 | 683 | 161.8 | 8.7 | [9 empty] | 0 | [13 empty] | ​Fahrenheit | mrh4 | Not Adjusted |  | 53.6 | 2015-09-21 10:17 | Jay Dahlstrom
293 | 1200 | 1200-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-11 09:14 | 677 | 152.7 | 8.7 | [9 empty] | 0.03 | [13 empty] | ​​Fahrenheit​ | mrh4 | Not Adjusted |  | 54 | 2015-09-21 09:16 | Jay Dahlstrom
294 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-18 10:19 | 562 |  |  | 93 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-10-01 10:19 | RICHARD A. JOHNSON
295 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-24 09:22 | 510 |  |  | 82 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-07-30 09:23 | RICHARD A. JOHNSON
296 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-21 10:30 | 487 |  |  | 192 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-05-31 10:30 | RICHARD A. JOHNSON
297 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-22 07:50 | 470 |  |  | 161 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 65 | 2018-04-02 07:51 | RICHARD A. JOHNSON
298 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-28 11:26 | 620 |  |  | 214 | [8 empty] | 0.1 | [13 empty] | ​turned on st70 pump for 30mins | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2018-03-16 11:29 | Daimon A. Boccamazzo
299 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-30 13:22 | 480 |  |  | 167 | [8 empty] | 0.7 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2018-02-01 13:23 | RICHARD A. JOHNSON
300 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-22 12:13 | 460 |  |  | 154 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 73 | 2017-12-04 12:14 | RICHARD A. JOHNSON
301 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:20 | 331 |  | 9.21 | 205 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-06-19 07:21 | RICHARD A. JOHNSON
302 | 1130 | 1130-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-04 14:02 | 135 | 0 | 7.6 | [9 empty] | 0.05 |  |  |  | 500647 |  |  |  |  | Not Correct | Good | Clean | Clean | Level Okay | Trasar feed pump was found unplugged. Plugged back in and system becang pumping hcemical into the system. free chlorine was low because it was a non feed day. Conductivity probe was reading inaccurate. This has happened several times, I will be sending a | reedhea |  |  |  | 2017-05-04 14:07 | reedhea
303 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-24 07:36 | [26 empty] | ​didn't have any water in the chemical loop. Tower wasn't running cause of the cold weather. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-26 07:38 | Daimon A. Boccamazzo
304 | 1130 | 1130-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-12-13 14:37 | 410 | 861 | 8.1 | [9 empty] | 0.51 |  |  |  | 497363 |  |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​​Conductivity recalibrated. Trasar inhibitor manually turned off for 48 hours. Sensor overfed chemistry on 12/6 according to trends. | reedhea |  |  |  | 2016-12-13 14:41 | reedhea
305 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-06 10:18 | 358 |  | 9.2 | 146 | [8 empty] | 0.2 | [13 empty] | ​changed st70 pump speed to 60 instead of 40 | Daimon A. Boccamazzo | Up | 60 | 66 | 2016-12-12 10:22 | Daimon A. Boccamazzo
306 | 1130 | 1130-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 11:41 | 289 | 113 | 7.6 | [9 empty] | 1.15 |  |  |  | 485618 |  |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​conductivity recalibrated. | reedhea |  |  |  | 2016-11-09 12:02 | reedhea
307 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-24 14:26 | 287 |  | 9 | 230 | [8 empty] | 6.4 | [13 empty] | ​conductivity sensor needs calibration | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-10-24 14:28 | Daimon A. Boccamazzo
308 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-25 10:08 | 309 |  | 8.6 | 210 | [8 empty] | 5.5 | [13 empty] | ​check conductivity calibration' controller is 635 and my meter is reading 309. St70 high because it just got done feeding at 6 and I tested tower at 8 | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-07-26 10:11 | Daimon A. Boccamazzo
309 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:39 | 182 |  | 8.6 | 139 | [8 empty] | 0.8 | [13 empty] | ​need to check calibration on the conductivity sensor, it is reading 816 and my meter is reading 182. Otherwise system is good with no leaks or problems. Strainer is good probably should be cleaned out next time around | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2016-06-02 13:42 | Daimon A. Boccamazzo
310 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-18 13:16 | 2136 |  | 9 | 375 | [8 empty] | 2.2 | [13 empty] | ​need to check calibration on cond and orp. The controller is reading 1539 and orp is reading 549. And I got 2136 on conductivity and 375 9pm orp | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-05-18 13:19 | Daimon A. Boccamazzo
311 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 10:37 | 1085 |  | 8.9 | 228 | [8 empty] | 0.04 | [13 empty] | ​no chemicals at all in the porta feeds. Pumps not plugged in. Adjusted pump speed on all three pumps to 60. Need bucket up here as well | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-09 10:41 | Daimon A. Boccamazzo
312 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-08 14:14 | 637 | 7 | 8.4 | 330 | [8 empty] | 3 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 71 | 2016-04-08 14:15 | Bob A Adams
313 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-28 06:52 | 319 | 4 | 8.4 | 385 | [8 empty] | 4 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 68 | 2016-03-29 06:56 | Bob A Adams
314 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-11 13:59 | 630 | 8 | 8.5 | 248 | [8 empty] | 0.6 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 71.5 | 2016-03-11 14:04 | Bob A Adams
315 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-26 06:39 | 220 | 8 | 8.4 | 300 | [8 empty] | 1.8 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 70 | 2016-02-29 06:41 | Bob A Adams
316 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-23 14:25 | 71 | 0 | 8.5 | 490 | [8 empty] | 2 | [13 empty] | ​makeup water is sticking on. | Bob A Adams | Not Adjusted |  | 65 | 2016-02-23 14:26 | Bob A Adams
317 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 08:50 | 76 | 2 | 8.4 | 310 | [8 empty] | 2 | [13 empty] | ​debri from cleaning in level probe piping | Bob A Adams | Not Adjusted |  | 76 | 2016-02-08 08:52 | Bob A Adams
318 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-12 14:27 | 341 | 5 | 8.4 | 171 | [8 empty] | 0 | [13 empty] | ​Posca in range. Cleaned sensors. Blow by need to look into | Bob A Adams | Not Adjusted |  | 75 | 2016-01-12 14:36 | Bob A Adams
319 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-30 14:44 | 367 | 2 | 8.4 | 177 | [8 empty] | 0 | [13 empty] | ​​calibrated orp and turned on pump | Bob A Adams | Not Adjusted |  | 69 | 2015-12-30 14:48 | Bob A Adams
320 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-06 11:13 | 486 | 6 | 8.1 | 281 | [8 empty] | 0 | [13 empty] | ​Prime both bromine and posca pumps CH20 treatment system | mrh4 | Not Adjusted |  | 66.3 | 2015-11-24 11:17 | mrh4
321 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-08 11:09 | 631 | 8 | 8 | 215 | [8 empty] | 6 | [13 empty] | ​CH20 system. Scale inhibitor is at 8ppm this within their parameters | mrh4 | Down |  | 19.6 | 2015-10-08 11:15 | mrh4
322 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-02 14:37 | 621 | 8 | 8.2 | 221 | [8 empty] | 2 | [13 empty] | ​​Cleaned side stream filter | mrh4 | Not Adjusted |  |  | 2015-10-02 14:40 | mrh4
323 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-14 13:37 | 595 |  | 8.1 | [23 empty] | ​​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 22.3 | 2015-09-21 13:37 | Jay Dahlstrom
324 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-10 13:32 | 591 |  | 8 | [23 empty] | TEI - 6 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 23.1 | 2015-09-21 13:33 | Jay Dahlstrom
325 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-01 12:54 | 607 |  | 8.1 | [23 empty] | ​​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 25.1 | 2015-09-21 12:54 | Jay Dahlstrom
326 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-04 10:22 | 590 |  | 8 | [23 empty] | ​TEI - 3 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 27.7 | 2015-09-21 10:23 | Jay Dahlstrom
327 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-25 10:14 | 609 |  | 8.1 | [23 empty] | ​​TEI - 3 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 26.9 | 2015-09-21 10:15 | Jay Dahlstrom
328 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-20 09:21 | 627 |  | 8.1 | [23 empty] | ​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.1 | 2015-09-21 09:22 | Jay Dahlstrom
329 | 1130 | 1130-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-22 09:05 | 586 |  | 8.1 | [23 empty] | ​TEI - 4 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 19.4 | 2015-09-21 09:05 | Jay Dahlstrom
330 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-19 10:08 | 407 |  |  | 227 | [8 empty] | 0.5 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 60 | 2018-10-01 10:09 | RICHARD A. JOHNSON
331 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:32 | 561 |  |  | 156 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 62 | 2018-08-30 11:33 | RICHARD A. JOHNSON
332 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 10:36 | 695 |  |  | 239 | [8 empty] | 8.8 | [13 empty] | ​tower fed st70 today which is why the FC levels are so high. Everything is all good. | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2018-08-10 10:38 | Daimon A. Boccamazzo
333 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 07:03 | 629 |  |  | 206 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 62 | 2018-07-03 07:04 | RICHARD A. JOHNSON
334 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-25 13:29 | 738 |  |  | 230 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 59 | 2018-04-30 13:30 | RICHARD A. JOHNSON
335 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-21 10:19 | 708 |  |  | 300 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 49 | 2018-02-23 10:20 | RICHARD A. JOHNSON
336 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-29 14:04 | 675 |  |  | 270 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2017-12-29 14:05 | RICHARD A. JOHNSON
337 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-18 10:35 | 669 |  |  | 354 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2017-10-23 10:37 | RICHARD A. JOHNSON
338 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:15 | 613 |  |  | 243 | [8 empty] | 6.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2017-08-24 08:16 | RICHARD A. JOHNSON
339 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:08 | 597 |  |  | 225 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2017-08-02 10:10 | RICHARD A. JOHNSON
340 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-05-02 08:46 | 700 |  | 8.7 | 120 | [8 empty] | 0 | [13 empty] | ​everything all good. Cleaned the strainer, conductivity sensor and the flow meter. FC will feed on Wednesday so I'm not worried about the low levels today. | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2017-05-16 08:51 | Daimon A. Boccamazzo
341 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-03 11:57 | 802 |  | 8.8 | 337 | [8 empty] | 1.1 | [13 empty] | ​everything is all good | Daimon A. Boccamazzo | Not Adjusted |  | 51 | 2017-01-17 12:00 | Daimon A. Boccamazzo
342 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-28 11:03 | 780 |  | 8.3 | 335 | [8 empty] | 8.8 | [13 empty] | ​free chlorine levels high because the system had just fed st70 into the tower | Daimon A. Boccamazzo | Not Adjusted |  | 58 | 2016-11-29 11:05 | Daimon A. Boccamazzo
343 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-03 08:53 | 720 |  | 8.8 | 380 | [8 empty] | 8.8 | [13 empty] | ​tower had just fed chemical into the system that's why the free chlorine levels were so high. Other than that everything else was all good | Daimon A. Boccamazzo | Not Adjusted |  | 60 | 2016-10-14 08:56 | Daimon A. Boccamazzo
344 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-02 14:18 | 686 |  | 8.4 | 255 | [8 empty] | 8.8 | [13 empty] | ​feed 2 missed (which is the st70) but the free chlorine levels are still high. Not sure why that is? | Daimon A. Boccamazzo | Not Adjusted |  | 64 | 2016-09-06 14:21 | Daimon A. Boccamazzo
345 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-26 10:23 | 667 |  | 8.6 | 289 | [8 empty] | 0.2 | [13 empty] | ​need to find out why relay 2 keeps missing its feed. | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-07-26 10:25 | Daimon A. Boccamazzo
346 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-07 09:14 | 645 |  | 8.6 | 245 | [8 empty] | 8.8 | [13 empty] | ​free chlorine is off the charts because it he tower just got done feeding st70 for an hour. Change st70 timer to mon-wed-fri for an hour at 6am. Cleaned strainer. | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2016-06-07 09:18 | Daimon A. Boccamazzo
347 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-23 10:08 | 913 |  | 8.6 | 250 | [8 empty] | 8.8 | [13 empty] | ​free chlorine off the charts because the system just got done feeding st70 into the tower an hour ago. Strainer still looking good | Daimon A. Boccamazzo | Not Adjusted |  | 60 | 2016-05-23 10:10 | Daimon A. Boccamazzo
348 | 1223 | 1223-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-22 23:59 | 954 | 90 | 8.5 |  | 210 | 180 |  |  | 5.1 | 10.8 | 1.56 | 1.8 | 6.8 | 0.087 | 0.4 |  |  | 391200 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Turned Trasar pump back on, fluorometer is calibrated. Turned down ST70 pump from 60 to 40, because of high Cl. | jrojas92 |  |  |  | 2016-06-07 00:04 | jrojas92
349 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 10:29 | 960 |  | 8.6 | 380 | [8 empty] | 2.2 | [13 empty] | ​need bucket up here. Reasoning for the free chlorine being up so high is cause it feeds every Monday, Wednesday, and Friday at 6am for an hour and I tested the tower at 8am. Cleaned chamical loop strainer | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-09 10:35 | Daimon A. Boccamazzo
350 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-05 14:25 | [12 empty] | 8.8 | [13 empty] | ​over 8ppm. Turned st70 pump speed back down to 60. Also switched the blowdown valve back on and turned it on auto. All systems are normal | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-05 14:27 | Daimon A. Boccamazzo
351 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-05 14:23 | [12 empty] | 8.8 | [13 empty] | ​over 8 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-05 14:25 | Daimon A. Boccamazzo
352 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 14:33 | [12 empty] | 8.8 | [13 empty] | ​over 8 ppm | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 14:34 | Daimon A. Boccamazzo
353 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 09:18 | [12 empty] | 8.8 | [13 empty] | ​pumped st70 into the system for 20 minutes and turned pump speed up from 60 to 80 also turned off RO water and switched the tower to city water for make up. First test was done at 8:30am 5/4/16. second test was done at 8:32am 5/4/16. Third test was done | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 09:22 | Daimon A. Boccamazzo
354 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 09:17 | [12 empty] | 0.1 | [13 empty] | ​see third entry for notes and details | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 09:18 | Daimon A. Boccamazzo
355 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-04 09:16 | [12 empty] | 0.3 | [13 empty] | ​see last entry for notes and details | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-04 09:17 | Daimon A. Boccamazzo
356 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-03 13:16 | [12 empty] | 8.8 | [13 empty] | ​free chlorine above meter range at 8:20 am 03MAY16 & over 8 ppm again at 1:15 pm 03MAY16 | dn3 | Not Adjusted |  |  | 2016-05-03 13:19 | dn3
357 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-03 08:35 | [12 empty] | 8.8 | [13 empty] | ​Readings were off the chart because I manually pumped st70 into the system for 20 to 30 minutes. First test was at 7:47, second test was at 8:18 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-03 08:39 | Daimon A. Boccamazzo
358 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-03 08:32 | [12 empty] | 0.3 | [13 empty] | ​turned the blowdown valve off. Also pumped st70 into the system and made adjustments to the pump speed on both the st70 and the h550. Turned the pumps to 60 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-03 08:35 | Daimon A. Boccamazzo
359 | 1223 | 1223-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-27 22:38 | 868 | 2690 | 5.6 |  | 130 | 276 |  | 0.14 | 96 | 13.4 |  | 18.3 | 0.02 | 0.791 | 0.04 |  |  | 391200 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Controller was reading 390ppm, so pump turned off because of really high level until calibration. | jrojas92 |  |  |  | 2016-06-06 22:47 | jrojas92
360 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-18 12:04 | 970 |  | 6.1 | 400 | [8 empty] | 8.8 | [13 empty] | ​orp is reading a negative number, alarm for a bad sensor, also drain some water out of the tower to bring the conductivity down | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-18 12:07 | Daimon A. Boccamazzo
361 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 14:05 | 1002 | 5.9 | 8.4 | 206 | [8 empty] | 0.1 | [13 empty] | Turned on st70 for five minutes. Waiting controller to be programmed ​ | Bob A Adams | Not Adjusted |  | 60.4 | 2016-03-31 14:10 | Bob A Adams
362 | 1223 | 1223-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-28 20:37 | 401 | 0 | 8.3 |  | 150 | 74 |  | 0.5 | 0.4 | 0 | 0.4 | 0 | 0.04 | 0.288 | 0.37 |  |  | 390100 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 20:43 | jrojas92
363 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-24 09:15 | 457 | 0 | 8.4 | 303 | [8 empty] | 0.1 | [13 empty] | ​chemicals on site waiting on Nalco to turn on set up controller. | Bob A Adams | Not Adjusted |  | 56 | 2016-03-24 09:17 | Bob A Adams
364 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 10:26 | 761 | 0 | 8.6 | 216 | [8 empty] | 0 | [13 empty] | ​Waiting for Nalco to deliver Chema. | Bob A Adams | Not Adjusted |  | 61 | 2016-03-10 10:29 | Bob A Adams
365 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-09 07:41 | 587 | 6 | 8.5 | 214 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Cleaned sensors. Last time testing with H2O. | Bob A Adams | Not Adjusted |  | 58.5 | 2016-02-09 07:46 | Bob A Adams
366 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-26 14:04 | 625 | 10 | 8.4 | 237 | [8 empty] | 0.8 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 58 | 2016-01-28 14:06 | Bob A Adams
367 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-14 06:51 | 673 | 10 | 8.7 | 350 | [8 empty] | 2 | [13 empty] | ​Posca in range. Cleaned Sensors. Calibrated conductivity and orp | Bob A Adams | Not Adjusted |  | 55 | 2016-01-14 06:54 | Bob A Adams
368 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-05 07:43 | 628 | 8 | 8.7 | 338 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Calibrated conductivity. Cleaned sensors | Bob A Adams | Not Adjusted |  | 54 | 2016-01-05 07:45 | Bob A Adams
369 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:34 | 640 | 6 | 8.6 | 241 | [8 empty] | 0.9 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 62 | 2015-12-31 07:38 | Bob A Adams
370 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 06:47 | 626 | 6 | 8.7 | 230 | [8 empty] | 1.8 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 61.2 | 2015-12-09 06:50 | Bob A Adams
371 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-02 06:54 | 624 | 8 | 8.6 | 269 | [8 empty] | 0.7 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 71 | 2015-12-04 06:58 | Bob A Adams
372 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-23 14:14 | 606 | 8 | 8.6 | 312 | [8 empty] | 1.3 | [13 empty] | ​​cleaned sensors. Posca in range | Bob A Adams | Not Adjusted |  | 66 | 2015-11-30 14:17 | Bob A Adams
373 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-12 13:47 | 604 | 6 | 8.5 | 360 | [8 empty] | 2 | [13 empty] | ​Posca is in range | Bob A Adams | Not Adjusted |  | 56.8 | 2015-11-16 13:50 | Bob A Adams
374 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-28 06:55 | 658 | 8 | 8.8 | 133 | [8 empty] | 0.3 | [13 empty] | ​Free chlorine and Posca in range | Bob A Adams | Not Adjusted |  | 63.2 | 2015-11-03 06:58 | Bob A Adams
375 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-27 14:24 | 602 | 10 | 8.6 | 262 | [8 empty] | 0.4 | [13 empty] | Posca and conductivity in range ​ | Bob A Adams | Not Adjusted |  | 60 | 2015-10-28 14:28 | Bob A Adams
376 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-09 08:19 | 583 | 4 | 8.5 | 300 | [8 empty] | 1.2 | [13 empty] | ​Posca and conductivity in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 65.7 | 2015-10-26 08:22 | Bob A Adams
377 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-25 12:28 | 588 |  | 8.6 | [23 empty] | ​ORP= 319 TWO= 1.9 OP= 6 | mrh4 | Not Adjusted |  | 65.6 | 2015-09-21 12:29 | Cesar Escobar
378 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-18 12:27 | 610 |  | 8.5 | [23 empty] | ​ORP= 290 TWO= .7 OP= 6 | mrh4 | Not Adjusted |  | 67 | 2015-09-21 12:28 | Cesar Escobar
379 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-11 12:26 | 547 |  | 8.6 | [23 empty] | ​ | mrh4 | Not Adjusted |  | 66.7 | 2015-09-21 12:27 | Cesar Escobar
380 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-04 12:25 | 665 |  | 8.5 | [23 empty] | ​ORP= 174 TWO= 0.1 OP= 8 | mrh4 | Not Adjusted |  | 63.3 | 2015-09-21 12:26 | Cesar Escobar
381 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-30 12:24 | 641 |  | 8.5 | [23 empty] | ​ORP= 238 TWO= .5 OP= 6 | mrh4 | Not Adjusted |  | 65.5 | 2015-09-21 12:24 | Cesar Escobar
382 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-05 12:22 | 584 |  | 8.5 | [23 empty] | ​ORP= 230 TWO= .4 OP= 6 | mrh4 | Not Adjusted |  | 60.1 | 2015-09-21 12:23 | Cesar Escobar
383 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-01 12:19 | 614 |  | 8.4 | [23 empty] | ​ORP= 245 TWO= .2 OP= 6 | mrh4 | Not Adjusted |  | 62.3 | 2015-09-21 12:22 | Cesar Escobar
384 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-19 12:07 | 590 |  | 8.5 | [23 empty] | ORP= 265 TWO= .4​ OP= 4 | mrh4 | Not Adjusted |  | 61.7 | 2015-09-21 12:19 | Cesar Escobar
385 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-12 12:06 | 565 |  | 8.4 | [23 empty] | ​ORP= 255 TWO= .9 OP= 10 | mrh4 | Not Adjusted |  | 61 | 2015-09-21 12:07 | Cesar Escobar
386 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-07 12:04 | 569 |  | 8.4 | [23 empty] | ​ORP= 271 TWO= .6 OP= 8 | mrh4 | Not Adjusted |  | 58.2 | 2015-09-21 12:05 | Cesar Escobar
387 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-06 12:03 | 579 |  | 8.5 | [23 empty] | ​ORP= 210 TWO= 0 OP= 8 | mrh4 | Not Adjusted |  | 57.9 | 2015-09-21 12:04 | Cesar Escobar
388 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-04 12:02 | 586 |  | 8.2 | [23 empty] | ​ORP= 202 TWO= 0 OP= 6 | mrh4 | Not Adjusted |  | 58 | 2015-09-21 12:03 | Cesar Escobar
389 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-23 12:01 | 612 |  | 8.6 | [23 empty] | ​ORP= 267 TWO= 0 OP= 6 | mrh4 | Not Adjusted |  | 57.4 | 2015-09-21 12:02 | Cesar Escobar
390 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 12:00 | 628 |  | 8.6 | [23 empty] | ​ORP= 295 TWO= .9 OP= 8 | mrh4 | Not Adjusted |  | 56.5 | 2015-09-21 12:01 | Cesar Escobar
391 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-21 11:59 | 575 |  | 8.4 | [23 empty] | ​ORP= 306 TWO= 2.1 OP= 4 | mrh4 | Not Adjusted |  | 60.6 | 2015-09-21 12:00 | Cesar Escobar
392 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 11:58 | 585 |  | 8.4 | [23 empty] | ​ORP= 305 TWO= 1.8 OP= 6 | mrh4 | Not Adjusted |  | 58.5 | 2015-09-21 11:59 | Cesar Escobar
393 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-16 13:52 | 557 |  | 7.9 | [23 empty] | ​TEI - 2 ppm POSCA - 10 ppm | mrh4 | Not Adjusted |  | 11.7 | 2015-09-21 13:53 | Jay Dahlstrom
394 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-09 11:57 | 607 |  | 8.5 | [23 empty] | ​TWO= 2.1 OP= 8 | mrh4 | Not Adjusted |  | 59.3 | 2015-09-21 11:58 | Cesar Escobar
395 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-17 11:56 | 622 |  | 8.5 | [23 empty] | ​ORP= 258 TWO= .6 OP= 8 | mrh4 | Not Adjusted |  | 60.5 | 2015-09-21 11:57 | Cesar Escobar
396 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-13 11:55 | 620 |  | 8.6 | [23 empty] | ​ORP= 244 TWO= 1.1 OP= 8 | mrh4 | Not Adjusted |  | 61.1 | 2015-09-21 11:56 | Cesar Escobar
397 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-11 11:54 | 628 |  | 8.5 | [23 empty] | ORP= 248 TWO= 1.2 OP= 6​ | mrh4 | Not Adjusted |  | 60.2 | 2015-09-21 11:55 | Cesar Escobar
398 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-05 11:53 | 600 |  | 8.6 | [23 empty] | ​ORP= 281 TWO= .8 OP= 8 | mrh4 | Not Adjusted |  | 55 | 2015-09-21 11:54 | Cesar Escobar
399 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-03 11:52 | 609 |  | 8.5 | [23 empty] | ​ORP= 280 TWO= .6 OP= 8 | mrh4 | Not Adjusted |  | 56.8 | 2015-09-21 11:52 | Cesar Escobar
400 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-26 11:51 | 629 |  | 8.1 | [23 empty] | ​ORP= 282 TWO= .5 OP= 8 | mrh4 | Not Adjusted |  | 56.7 | 2015-09-21 11:51 | Cesar Escobar
401 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-23 11:49 | 615 |  | 8.3 | [23 empty] | ​ORP= 269 TWO= .4 OP= 8 | mrh4 | Not Adjusted |  | 57.2 | 2015-09-21 11:50 | Cesar Escobar
402 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-18 11:48 | 605 |  | 8.4 | [23 empty] | ​ORP= 278 TWO= .8 OP= 10 | mrh4 | Not Adjusted |  | 56.9 | 2015-09-21 11:49 | Cesar Escobar
403 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-10 11:35 | 552 |  | 8.4 | [23 empty] | ​ORP= 337 TWO= 1.9 OP= 8 | mrh4 | Not Adjusted |  | 60.9 | 2015-09-21 11:48 | Cesar Escobar
404 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-05 11:34 | 635 |  | 8.5 | [23 empty] | ​ORP= 237 TWO= 1.4 OP= 10 | mrh4 | Not Adjusted |  | 59.9 | 2015-09-21 11:35 | Cesar Escobar
405 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-27 11:32 | 638 |  | 8.6 | [23 empty] | ​ORP= 260 TWO= 2.6 OP= 8 | mrh4 | Not Adjusted |  | 60.7 | 2015-09-21 11:34 | Cesar Escobar
406 | 1223 | 1223-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-21 11:30 | 653 |  | 8.3 | [23 empty] | ​ORP= 380 OP= 8 | mrh4 | Not Adjusted |  | 54.2 | 2015-09-21 11:31 | Cesar Escobar
430 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-24 11:03 | 110 | 0 | 8.4 | 235 | [8 empty] | 0.1 | [13 empty] | ​Nalco has not set up controller . | Bob A Adams | Not Adjusted |  | 70.3 | 2016-03-24 11:10 | Bob A Adams
431 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-16 14:08 | 321 | 1 | 8.3 | 218 | [8 empty] | 0.8 | [13 empty] | ​will be on Nalco for next test | Bob A Adams | Not Adjusted |  | 68.8 | 2016-03-16 14:10 | Bob A Adams
432 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-08 06:46 | 763 | 7 | 8.3 | 483 | [8 empty] | 5 | [13 empty] | ​posca in range. Orp sensor needed calibration. | Bob A Adams | Not Adjusted |  | 70 | 2016-03-08 06:49 | Bob A Adams
433 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-26 06:35 | 746 | 6 | 8.5 | 305 | [8 empty] | 1.4 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 65 | 2016-02-29 06:38 | Bob A Adams
434 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-25 13:53 | 563 | 8 | 8.5 | 269 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Cleaned sensors. | Bob A Adams | Not Adjusted |  | 67 | 2016-01-25 13:55 | Bob A Adams
435 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-12 07:02 | 288 | 4 | 8.4 | 162 | [8 empty] | 0 | [13 empty] | ​Posca in range. Cleaned sensors. Calibrated orp. Pump lost prime | Bob A Adams | Not Adjusted |  | 72 | 2016-01-12 07:04 | Bob A Adams
436 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-05 11:03 | 245 | 2 | 8.5 | 314 | [8 empty] | 0 | [13 empty] | ​There was no water coming out of f drain line. Leak in loop must be increasing | Bob A Adams | Not Adjusted |  | 71.4 | 2016-01-05 11:06 | Bob A Adams
437 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 06:40 | 606 | 2 | 8.6 | 252 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 66.8 | 2015-12-09 06:44 | Bob A Adams
438 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-01 06:49 | 610 | 6 | 8.5 | 315 | [8 empty] | 1.2 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 56 | 2015-12-04 06:52 | Bob A Adams
439 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-30 13:53 | 418 | 6 | 8.5 | 286 | [8 empty] | 0.8 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 69 | 2015-11-30 13:55 | Bob A Adams
440 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-12 13:53 | 591 | 6 | 8.5 | 330 | [8 empty] | 1.4 | [13 empty] | ​Posca in range. Cleaned the sensors | Bob A Adams | Not Adjusted |  | 71 | 2015-11-16 13:56 | Bob A Adams
441 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-06 14:16 | 574 | 4 | 8.5 | 370 | [8 empty] | 2 | [13 empty] | Posca and conductivity in range. Cleaned sensors ans set time.​ | Bob A Adams | Not Adjusted |  | 74 | 2015-11-06 14:22 | Bob A Adams
442 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-27 14:35 | 587 | 8 | 8.5 | 289 | [8 empty] | 0.8 | [14 empty] | Bob A Adams | Not Adjusted |  | 68 | 2015-10-28 14:37 | Bob A Adams
443 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-20 08:45 | 599 |  | 8.5 | [23 empty] | ​​ORP = 281 TWO = 0.6 OP = 6 | mrh4 | Not Adjusted |  | 71 | 2015-09-24 08:46 | Marilyn Fick
444 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-20 08:41 | 599 |  | 8.5 | [23 empty] | ​ORP = 277 TWO = 1.5 OP = 6 | mrh4 | Not Adjusted |  | 71 | 2015-09-24 08:42 | Marilyn Fick
445 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-12 08:40 | 584 |  | 8.5 | [23 empty] | ​ORP = 277 TWO = 1.5 OP = 6 | mrh4 | Not Adjusted |  | 70 | 2015-09-24 08:41 | Marilyn Fick
446 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-10 08:40 | [26 empty] | ​OUT OF BROMINE, REPLACED & CLEANED SENSORS​ | mrh4 | Not Adjusted |  |  | 2015-09-24 08:40 | Marilyn Fick
447 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-06 08:38 | 587 |  | 8.5 | [23 empty] | ​ORP = 270 TWO = 1.5 OP = 4 | mrh4 | Not Adjusted |  | 72.1 | 2015-09-24 08:40 | Marilyn Fick
448 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-04 08:37 | 616 |  | 8.5 | [23 empty] | ​ORP = 255 TWO = 1.9 OP = 6 | mrh4 | Not Adjusted |  | 70.7 | 2015-09-24 08:38 | Marilyn Fick
449 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-24 08:36 | 573 |  | 8.6 | [23 empty] | ​ORP = 275 TWO = 1.2 OP = 4 REPLACED POSCA, ON FOR 10 MIN | mrh4 | Not Adjusted |  | 74.8 | 2015-09-24 08:37 | Marilyn Fick
450 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-23 08:35 | [26 empty] | ​BROMINE PUMPING CLEANED SENSORS | mrh4 | Not Adjusted |  |  | 2015-09-24 08:36 | Marilyn Fick
451 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-01 08:34 | 597 |  | 8.5 | [23 empty] | ​ORP = 312​ TWO = 1.0 OP = 2 POSCA ON 10 MIN | mrh4 | Not Adjusted |  | 73.2 | 2015-09-24 08:35 | Marilyn Fick
452 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-18 08:33 | 580 |  | 8.4 | [23 empty] | ​​ORP = 320 TWO = 0.7 OP = 4 PRIMED POSCA | mrh4 | Not Adjusted |  | 71.3 | 2015-09-24 08:34 | Marilyn Fick
453 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-12 08:32 | 586 |  | 8.5 | [23 empty] | ​ORP = 315 TWO = 1.2 OP = 6 | mrh4 | Not Adjusted |  | 73.6 | 2015-09-24 08:33 | Marilyn Fick
454 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-29 08:30 | 586 |  | 8.5 | [23 empty] | ​ORP = 324 TWO = 1.5 OP = 2 POSCA 10 ON | mrh4 | Not Adjusted |  | 69.7 | 2015-09-24 08:32 | Marilyn Fick
455 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 08:29 | 637 |  | 8.6 | [23 empty] | ​ORP = 72 TWO = 0 OP = 4 | mrh4 | Not Adjusted |  | 72.2 | 2015-09-24 08:30 | Marilyn Fick
456 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 08:28 | 623 |  | 8.5 | [23 empty] | ​ORP = 70 TWO = 0 OP = 6 | mrh4 | Not Adjusted |  | 69.4 | 2015-09-24 08:28 | Marilyn Fick
457 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-16 13:53 | 573 |  | 7.9 | [23 empty] | TEI - 0 ppm ​POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.5 | 2015-09-21 13:54 | Jay Dahlstrom
458 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-07 08:26 | 639 |  | 8 | [23 empty] | ​ORP = 190 TWO = 0.2 OP = 2 POSCA ON 10 MIN | mrh4 | Not Adjusted |  | 70 | 2015-09-24 08:27 | Marilyn Fick
459 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-07 08:20 | 639 |  | 8 | [23 empty] | ​ORP = 325 TWO = 1.1 OP = 2 | mrh4 | Not Adjusted |  | 70 | 2015-09-24 08:20 | Marilyn Fick
460 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-02 08:11 | 611 |  | 8 | [23 empty] | ​ORP = 325 TWO = 1.1 OP = 2 | mrh4 | Not Adjusted |  | 71 | 2015-09-24 08:20 | Marilyn Fick
461 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-26 08:10 | 447 |  | 7.8 | [23 empty] | ​ORP = 345​ TWO = 1.8 OP = 4 | mrh4 | Not Adjusted |  | 71.2 | 2015-09-24 08:11 | Marilyn Fick
462 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-04 08:09 | 370 |  | 8.5 | [23 empty] | ​ORP = 373 TWO = 2.1 OP = 2 | mrh4 | Not Adjusted |  | 54.6 | 2015-09-24 08:10 | Marilyn Fick
463 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-02 08:08 | 345 |  | 8.4 | [23 empty] | ​ORP = 340 TWO = 1.9 OP = 4 | mrh4 | Not Adjusted |  | 55.1 | 2015-09-24 08:09 | Marilyn Fick
464 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-18 08:07 | 437 |  | 8.4 | [23 empty] | ​​ORP = 212 TWO = 0.4 OP = 6 | mrh4 | Not Adjusted |  | 61.2 | 2015-09-24 08:08 | Marilyn Fick
465 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-10 08:06 | 585 |  | 8.5 | [23 empty] | ​ORP = 298 TWO = 0.8 OP = 6 | mrh4 | Not Adjusted |  | 69.8 | 2015-09-24 08:07 | Marilyn Fick
466 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-28 08:05 | 570 |  | 8.6 | [23 empty] | ​ORP = 350 TWO = 1.6 OP = 6​ POSCA 60-65 | mrh4 | Not Adjusted |  | 70.6 | 2015-09-24 08:06 | Marilyn Fick
467 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-21 08:01 | 614 |  | 8.4 | [23 empty] | ​ORP = 331 TWO = 1.5 OP = 2 | mrh4 | Not Adjusted |  | 70.2 | 2015-09-24 08:05 | Marilyn Fick
468 | 1228 | 1228-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-05 08:00 | 619 |  | 8.6 | [23 empty] | ​ORP = 314 TWO = 1.5​ OP = 8 | mrh4 | Not Adjusted |  | 71 | 2015-09-24 08:01 | Marilyn Fick
469 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-22 06:50 | 245 | 0 | 8.1 | 227 | [8 empty] | 0.1 | [14 empty] | Bob A Adams | Not Adjusted |  | 71.4 | 2016-02-22 07:02 | Bob A Adams
470 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-19 12:47 | 214 | 0 | 8.3 | 705 | [8 empty] | 23 | [13 empty] | ​Bleed for 10 minutes | Bob A Adams | Not Adjusted |  | 74.3 | 2016-02-19 12:49 | Bob A Adams
471 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-19 11:13 | 237 | 0 | 8 | 730 | [8 empty] | 30 | [13 empty] | ​bleed and retesting in 2 hrs | Bob A Adams | Not Adjusted |  | 72.7 | 2016-02-19 11:15 | Bob A Adams
472 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-19 09:51 | 265 | 0 | 8.1 | 724 | [8 empty] | 42 | [13 empty] | ​bleed for 10 minutes | Bob A Adams | Not Adjusted |  | 75.1 | 2016-02-19 09:53 | Bob A Adams
473 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-18 14:18 | 183 | 0 | 8.4 | 678 | [8 empty] | 32 | [13 empty] | Will monitor and retest in 30 minutes ​ | Bob A Adams | Not Adjusted |  | 72.2 | 2016-02-18 14:20 | Bob A Adams
474 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-18 13:25 | 170 | 0 | 8.3 | 690 | [8 empty] | 35 | [13 empty] | ​will wait until 2:30 and test again | Bob A Adams | Not Adjusted |  | 71.5 | 2016-02-18 13:27 | Bob A Adams
475 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-18 11:57 | 760 | 0 | 8.4 | 712 | [8 empty] | 80 | [13 empty] | ​Free chlorine was 80 plus. Bleeding and retesting | Bob A Adams | Not Adjusted |  | 67 | 2016-02-18 11:58 | Bob A Adams
476 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-18 11:55 | 1435 | 0 | 8.7 | 710 | [8 empty] | 80 | [13 empty] | ​Free chlorine was 80 plus. Bleeding and retesting | Bob A Adams | Not Adjusted |  | 69.3 | 2016-02-18 11:57 | Bob A Adams
477 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-18 11:52 | 2637 | 0 | 9 | 675 | [8 empty] | 80 | [13 empty] | ​Free chlorine is plus 80. Bleeding and retesting | Bob A Adams | Not Adjusted |  | 72.2 | 2016-02-18 11:55 | Bob A Adams
478 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-11 08:21 | 354 | 4 | 8.5 | 147 | [8 empty] | 0 | [13 empty] | ​Posca in range. Put new bag of pellets in feeder. | Bob A Adams | Not Adjusted |  | 73 | 2016-02-12 08:25 | Bob A Adams
479 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-15 14:05 | 644 | 8 | 8.4 | 225 | [8 empty] | 0.2 | [13 empty] | ​Posca in range. Tower is building conductivity after fixing soliniod valve leak | Bob A Adams | Not Adjusted |  | 74 | 2016-01-15 14:07 | Bob A Adams
480 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-05 11:06 | 157 | 3 | 8.3 | 218 | [8 empty] | 0.1 | [13 empty] | ​no water draining. Wondering if city water valve is properly closed in basement mechanical room | Bob A Adams | Not Adjusted |  | 74 | 2016-01-05 11:10 | Bob A Adams
481 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:44 | 521 | 6 | 8.3 | 231 | [8 empty] | 0.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 69 | 2015-12-31 07:46 | Bob A Adams
482 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-06 14:25 | 651 | 6 | 8.4 | 351 | [8 empty] | 0.1 | [13 empty] | ​Posca in range. | Bob A Adams | Not Adjusted |  | 70.9 | 2015-11-06 14:28 | Bob A Adams
483 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-28 07:04 | 605 | 16 | 8.4 | 315 | [8 empty] | 0.1 | [13 empty] | ​ | Bob A Adams | Not Adjusted |  | 65 | 2015-11-03 07:06 | Bob A Adams
484 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-01 14:08 | 186 | 4 | 8.5 | 235 | [8 empty] | 1.3 | [13 empty] | ​Posca in range. Tower leaks and makes up a lot of water. | Bob A Adams | Not Adjusted |  | 68.1 | 2015-10-01 14:13 | Bob A Adams
485 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-17 13:55 | 533 |  | 7.7 | [23 empty] | TEI - 2 ppm POSCA - 10 ppm​ | mrh4 | Not Adjusted |  | 19.7 | 2015-09-21 13:56 | Jay Dahlstrom
486 | 1174 | 1174-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-15 13:42 | 884 |  | 8.1 | [23 empty] | TEI - 1 ppm POSCA - 20+ ppm​ | mrh4 | Not Adjusted |  | 22.9 | 2015-09-21 13:43 | Jay Dahlstrom
487 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-09-24 10:13 | 861 |  |  | 218 | [8 empty] | 8.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 82 | 2018-10-01 10:14 | RICHARD A. JOHNSON
488 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-08-23 11:38 | 778 |  |  | 112 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2018-08-30 11:39 | RICHARD A. JOHNSON
489 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2018-08-23 11:38 | 802 |  |  | 121 | [8 empty] | 7.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-08-30 11:38 | RICHARD A. JOHNSON
490 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-07-31 10:53 | 736 |  |  | 185 | [8 empty] | 0 | [13 empty] | ​cleaned strainer and fed st70 into the system to bring the FC levels up. | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2018-08-10 10:55 | Daimon A. Boccamazzo
491 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2018-07-31 10:50 | 841 |  |  | 191 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer. System started feeding st70 after I was done testing it. | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2018-08-10 10:52 | Daimon A. Boccamazzo
492 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-06-29 07:00 | 828 |  |  | 208 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2018-07-03 07:00 | RICHARD A. JOHNSON
493 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2018-06-29 06:59 | 876 |  |  | 229 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2018-07-03 06:59 | RICHARD A. JOHNSON
494 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-04-23 13:25 | 588 |  |  | 268 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2018-04-30 13:26 | RICHARD A. JOHNSON
495 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2018-02-22 10:14 | 2829 |  |  | 93 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 49 | 2018-02-23 10:14 | RICHARD A. JOHNSON
496 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2018-02-22 10:13 | 2299 |  |  | 94 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 47 | 2018-02-23 10:13 | RICHARD A. JOHNSON
497 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-12-29 14:02 | 2735 |  |  | 114 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2017-12-29 14:02 | RICHARD A. JOHNSON
498 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2017-12-29 14:01 | 3099 |  |  | 210 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 55 | 2017-12-29 14:02 | RICHARD A. JOHNSON
499 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-10-20 10:47 | 844 |  |  | 253 | [8 empty] | 4.8 | [13 empty] | ​ | RICHARD A. JOHNSON | Not Adjusted |  | 64 | 2017-10-23 10:48 | RICHARD A. JOHNSON
500 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2017-10-20 10:45 | 761 |  |  | 265 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 64 | 2017-10-23 10:46 | RICHARD A. JOHNSON
501 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-08-24 08:33 | 918 |  |  | 340 | [8 empty] | 5.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-08-24 08:34 | RICHARD A. JOHNSON
502 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2017-08-24 08:31 | 808 |  |  | 296 | [8 empty] | 7.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-08-24 08:33 | RICHARD A. JOHNSON
503 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-08-02 10:04 | 829 |  |  | 210 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 75 | 2017-08-02 10:06 | RICHARD A. JOHNSON
504 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2017-08-02 10:03 | 737 |  |  | 132 | [8 empty] | 0.2 | [13 empty] | ​tested on off day | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2017-08-02 10:04 | RICHARD A. JOHNSON
505 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2017-01-05 13:11 | 2675 |  | 8.9 | 194 | [8 empty] | 0.2 | [13 empty] | ​testing tower before putting it in winter mode. Fed st70 in the system for 30 mins to bring the free chlorine levels up before shutting the tower down | Daimon A. Boccamazzo | Not Adjusted |  | 43 | 2017-01-17 13:15 | Daimon A. Boccamazzo
506 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2017-01-05 13:08 | 1370 |  | 8.9 | 198 | [8 empty] | 1.3 | [13 empty] | ​​testing the tower before putting it in winter mode | Daimon A. Boccamazzo | Not Adjusted |  | 42 | 2017-01-17 13:10 | Daimon A. Boccamazzo
507 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-11-29 11:33 | 1512 |  | 8.5 | 174 | [8 empty] | 0.2 | [13 empty] | ​conductivity probe needs calibration. Probe is reading 1282 | Daimon A. Boccamazzo | Not Adjusted |  | 58 | 2016-11-29 11:35 | Daimon A. Boccamazzo
508 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-11-29 11:28 | 862 |  | 8.4 | 185 | [8 empty] | 0.3 | [13 empty] | ​adjusted st70 pump from 40 to 60 | Daimon A. Boccamazzo | Up | 60 | 56 | 2016-11-29 11:32 | Daimon A. Boccamazzo
509 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-10-04 09:09 | 693 |  | 9.1 | 287 | [8 empty] | 0 | [13 empty] | ​​turned st70 pump to 80% instead of 60% because tower just isn't getting enough chemical pumping at that speed with how little the feeding time frame is. Also fixed a leak on the h-550 pump | Daimon A. Boccamazzo | Up | 80 | 75 | 2016-10-14 09:12 | Daimon A. Boccamazzo
510 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-10-04 09:07 | 763 |  | 9 | 230 | [8 empty] | 2.1 | [14 empty] | Daimon A. Boccamazzo | Not Adjusted |  | 63 | 2016-10-14 09:09 | Daimon A. Boccamazzo
511 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-09-06 14:35 | 1026 |  | 8.8 | 142 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Free chlorine levels low because I tested on Tuesday and the system feeds every Monday, Wednesday, and friday | Daimon A. Boccamazzo | Up | 60 | 67 | 2016-09-06 14:38 | Daimon A. Boccamazzo
512 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-09-06 14:32 | 779 |  | 8.6 | 135 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer, flow and conductivity sensors, free chlorine levels so low because I tested on Tuesday and the system feeds on modal, Wednesday, and Friday | Daimon A. Boccamazzo | Up | 60 | 61 | 2016-09-06 14:35 | Daimon A. Boccamazzo
513 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-07-28 13:51 | 701 |  | 8.8 | 196 | [8 empty] | 0.1 | [13 empty] | ​strainer is good just need to find out how to change the timer on the st70 | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2016-07-29 13:55 | Daimon A. Boccamazzo
514 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-07-28 13:46 | 790 |  | 8.7 | 140 | [8 empty] | 4.6 | [13 empty] | ​cleaned conductivity sensor and strainer. Need to get corrosion probe checked, alarm on #2 probe | Daimon A. Boccamazzo | Not Adjusted |  | 71 | 2016-07-29 13:51 | Daimon A. Boccamazzo
515 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-06-29 11:55 | 722 |  | 8.9 | 261 | [8 empty] | 2.7 | [13 empty] | ​cleaned strainer, flow sensor, and conductivity sensor. No problems everything in check | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-06-29 11:57 | Daimon A. Boccamazzo
516 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-06-29 11:52 | 742 |  | 8.9 | 272 | [8 empty] | 4.8 | [13 empty] | ​cleaned strainer, flow sensor, and conductivity sensor. They will definitely need to be cleaned next time around if they are as bad as they were today | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-06-29 11:55 | Daimon A. Boccamazzo
517 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-05-24 11:49 | 685 |  | 8.8 | 170 | [8 empty] | 0.5 | [13 empty] | ​strainer is good. Checked both towers and they both look good with no problems or leaks also conductivity sensor was calibrated on tower 1 | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-05-26 11:54 | Daimon A. Boccamazzo
518 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-05-24 11:44 | 798 |  | 8.9 | 160 | [8 empty] | 0.3 | [13 empty] | ​need to find out and label which relay is which. Would like to change the time settings on the st70. Cleaned strainer. | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-05-26 11:49 | Daimon A. Boccamazzo
519 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2016-05-22 23:52 | 670 | 372 | 8.6 |  | 220 | 182 |  |  | 0.9 | 14.2 | 1.02 | 15 | 1.31 | 0.106 | 0.13 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​Connected corrosion probes to controller. | jrojas92 |  |  |  | 2016-06-06 23:54 | jrojas92
520 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-22 23:46 | 871 | 130 | 8.6 |  | 250 | 260 |  |  | 0.8 | 4.5 | 0.3 | 0 | 0.83 | 0.095 | 0.1 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​Calibrated conductivity, 2-point. | jrojas92 |  |  |  | 2016-06-06 23:52 | jrojas92
521 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-05-10 12:23 | 705 |  | 8.6 | 221 | [8 empty] | 0.2 | [13 empty] | ​system good. Reasoning for low free chlorine level is cause the st70 is on the same schedule as tower 1 | Daimon A. Boccamazzo | Not Adjusted |  | 72 | 2016-05-10 12:27 | Daimon A. Boccamazzo
522 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-05-10 12:18 | 894 |  | 8.6 | 216 | [8 empty] | 0.02 | [13 empty] | ​reasoning for free chlorine being so low is the st70 is scheduled for 15 mins Monday through Friday at 10am and I tested at 730 am. Cleaned Chemical loop strainer on tower 1 | Daimon A. Boccamazzo | Not Adjusted |  | 64 | 2016-05-10 12:23 | Daimon A. Boccamazzo
523 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2016-04-27 22:27 | 642 | 791 | 8.5 |  | 220 | 200 |  | 2.42 | 2.1 | 12 | 2.17 | 37 | 0 | 0.092 | 0.28 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​ | jrojas92 |  |  |  | 2016-06-06 22:32 | jrojas92
524 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-27 22:22 | 811 | 114 | 8.4 |  | 170 | 218 |  | 0.82 | 1 | 2 | 0.8 | 0 | 0 | 0.136 | 0.14 | [6 empty] | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 22:27 | jrojas92
525 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-04-21 07:06 | 670 |  | 7.5 | 380 | [8 empty] | 8.8 | [13 empty] | ​free chlorine was off the charts when I tested it. Best conclusion for that is because the st70 and the 3dt222 were set to pump every day for 15 minute intervals once a day and pump speed at over 100, so adjusted the all three pumps. St70 and 3dt222 at 4 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-21 07:14 | Daimon A. Boccamazzo
526 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-04-20 07:14 | 760 |  | 8.3 | 308 | [8 empty] | 0 | [13 empty] | ​made adjustments to pump speeds same as the first tower. But the st70 for this tower was on zero so adjusted it to 40. Also cleaned out the chemical loop strainer | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-21 07:19 | Daimon A. Boccamazzo
527 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2016-04-04 10:55 | 570 | 0 | 8.3 | 310 | [8 empty] | 0 | [13 empty] | ​Tower is running. Controllers are not turned on. Waiting for booster pump to be started​ | Bob A Adams | Not Adjusted |  | 74 | 2016-04-04 10:56 | Bob A Adams
528 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2016-04-04 10:51 | 359 | 0 | 8.8 | 600 | [8 empty] | 8.4 | [13 empty] | ​​Tower is not running. Controllers are not turned on. Waiting for booster pump to be started. | Bob A Adams | Not Adjusted |  | 57 | 2016-04-04 10:54 | Bob A Adams
529 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2016-03-28 20:27 | 1097 |  | 8.8 |  | 40 | [5 empty] | 1.19 |  | 160 | 0.296 | 1.73 | [11 empty] | ​​Tower was BD for ~15min to reduce high Cl. Tower was off. | jrojas92 |  |  |  | 2016-06-06 20:30 | jrojas92
530 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-28 20:20 | 1112 | 0 | 8.7 |  | 50 | 52 |  | 0.44 | 1.8 | 0 | 1.17 | 0 | 172 | 0.165 | 0.46 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​Tower was BD for ~15min to reduce high Cl. Tower was off for repairs. | jrojas92 |  |  |  | 2016-06-06 20:26 | jrojas92
531 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2015-11-24 14:08 | 655 |  | 8.7 |  | 270 | 280 |  | 8.8 | 0.8 |  | 0.63 | 3 | 0.03 | 0.0882 | 0.16 | [7 empty] | Good | Clean | Clean |  |  | jrojas92 |  |  |  | 2015-12-22 14:10 | jrojas92
532 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 14:04 | 93 | 10 | 8.9 |  | 50 | 40 |  | 0.1 | 0.5 | 0 | 0.41 | 0.3 | 0.01 | 0.0319 | 0.08 | [6 empty] | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-12-22 14:07 | jrojas92
533 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-11-16 14:00 | 577 | 4 | 8.7 | 145 | [8 empty] | 0.1 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 62.8 | 2015-11-16 14:03 | Bob A Adams
534 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2015-10-29 15:28 | 572 |  | 8.4 |  | 280 | 238 |  | 3.9 | 0.4 |  | 0.61 | 2 | 0.02 | 0.033 | 0.05 | [12 empty] | jrojas92 |  |  |  | 2015-11-14 15:30 | jrojas92
535 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-29 15:25 | 308 | 130 | 8.1 |  | 90 | 96 |  | 1.11 | 2.5 | 6.8 | 0.56 | 0.7 | 1.07 | 0 | 0.08 | [6 empty] | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 15:28 | jrojas92
536 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2015-10-28 13:57 | 382 |  | 8.5 | 319 | [8 empty] | 6.1 | [13 empty] | ​Trasar meter not calibrated | Bob A Adams | Not Adjusted |  | 78.2 | 2015-11-16 14:00 | Bob A Adams
537 | 1173 | 1173-Cooling_Tower_2-UW | Cooling Tower | UW | 2015-10-28 06:39 | 63 |  | 8.5 | 145 | [8 empty] | 0.1 | [13 empty] | ​Trasar meter not working. | Bob A Adams | Not Adjusted |  | 62.8 | 2015-11-04 06:41 | Bob A Adams
538 | 1173 | 1173-Cooling_Tower_1-UW | Cooling Tower | UW | 2015-10-28 06:36 | 382 |  | 8.5 | 319 | [8 empty] | 6.1 | [13 empty] | ​Trasar meter not working. | Bob A Adams | Not Adjusted |  | 78.2 | 2015-11-04 06:39 | Bob A Adams
539 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2015-09-29 19:09 | 637 |  | 8.6 |  | 290 | 298 |  | 3.46 | 0 |  | 0.31 | 0.8 | 0.01 | 0.0346 | 0.11 | [7 empty] | Good |  |  |  |  | jrojas92 |  |  |  | 2015-09-30 19:12 | jrojas92
540 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-29 19:05 | 302 | 144 | 8.2 |  | 120 | 104 |  | 1.17 | 2.6 | 7 | 0.66 | 0.6 | 0 | 0.0566 | 0.13 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​There appears to be water loss from tower through the drain pipe, a small stream. | jrojas92 |  |  |  | 2015-09-30 19:09 | jrojas92
541 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2015-08-26 17:02 | 632 |  | 8.5 |  | 290 | 280 |  | 3.55 | 0.5 |  | 0.41 | 2.9 | 0.04 | 0.0518 | 0.16 | [12 empty] | jrojas92 |  |  |  | 2015-11-14 17:04 | jrojas92
542 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-26 16:59 | 364 | 131 | 8.3 |  | 160 | 138 |  | 1.32 | 3.2 | 4.4 | 0.3 | 0.7 | 0 | 0.0694 | 0.09 | [6 empty] | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 17:02 | jrojas92
543 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-07-16 14:00 | 955 | 33.9 | 8.8 |  | 200 | 294 |  | 0.42 | 0.2 | 0 | 0.22 | 0.4 | 0.03 | 0.0546 | 0.09 | [7 empty] | Good | Clean | Clean | Level Okay | ​There was no flow through the controller. Cooling tower pump was reset and flow started through the controller. | jrojas92 |  |  |  | 2015-08-18 14:06 | jrojas92
544 | 1173 | 1173-Cooling_Tower_2-NALCO | Cooling Tower | NALCO | 2015-06-25 17:53 | 97 |  | 7.9 |  | 50 | 44 |  | 2.06 | 1 |  | 0.52 | 0.9 | 0.03 | 0.0098 | 0.09 | [12 empty] | jrojas92 |  |  |  | 2015-11-14 17:54 | jrojas92
545 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-25 17:49 | 1668 | 64 | 8.4 |  | 430 | 442 |  | 0.75 | 0.7 | 0 | 0.04 | 0.5 | 0.05 | 0.0819 | 0.07 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | There was no flow through controller (high conductivity,etc). | jrojas92 |  |  |  | 2015-11-14 17:53 | jrojas92
546 | 1173 | 1173-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-28 18:37 | 836 | 127 | 8.7 |  | 330 | 318 |  | 1.58 | 3.1 | 6.2 | 0.25 | 0.9 | 0.34 | 0.0695 | 0.2 | [12 empty] | jrojas92 |  |  |  | 2015-11-14 18:39 | jrojas92
547 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-19 10:07 | 839 |  |  | 249 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-10-01 10:08 | RICHARD A. JOHNSON
548 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:35 | 780 |  |  | 132 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 68 | 2018-08-30 11:35 | RICHARD A. JOHNSON
549 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 10:31 | 728 |  |  | 215 | [8 empty] | 8.8 | [13 empty] | ​tower fed st70 today. Still need to install the pump for h550. Other than that everything is all good | Daimon A. Boccamazzo | Not Adjusted |  | 83 | 2018-08-10 10:34 | Daimon A. Boccamazzo
550 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 07:04 | 797 |  |  | 238 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-07-03 07:05 | RICHARD A. JOHNSON
551 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-25 13:30 | 781 |  |  | 308 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-04-30 13:31 | RICHARD A. JOHNSON
552 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-21 10:21 | 736 |  |  | 350 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 65 | 2018-02-23 10:22 | RICHARD A. JOHNSON
553 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-29 14:03 | 635 |  |  | 312 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2017-12-29 14:04 | RICHARD A. JOHNSON
554 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-18 10:31 | 657 |  |  | 421 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-10-23 10:34 | RICHARD A. JOHNSON
555 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:13 | 484 |  |  | 157 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2017-08-24 08:14 | RICHARD A. JOHNSON
556 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 07:39 | 504 |  |  | 142 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 80 | 2017-08-02 07:40 | RICHARD A. JOHNSON
557 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-05-02 08:41 | 600 |  | 9.3 | 100 | [8 empty] | 0 | [13 empty] | ​not worried about the low FC levels because the tower is scheduled to feed on Wednesday. | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2017-05-16 08:45 | Daimon A. Boccamazzo
558 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-03 11:51 | 690 |  | 8.7 | 290 | [8 empty] | 8.8 | [13 empty] | ​free chlorine high because the system had fed st70 the day before I had tested it. Changed feeding cycle to 20 mins instead of 30 so the the free chlorine levels aren't to high all the time | Daimon A. Boccamazzo | Not Adjusted |  | 62 | 2017-01-17 11:56 | Daimon A. Boccamazzo
559 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-28 10:59 | 740 |  | 8.5 | 270 | [8 empty] | 8.8 | [13 empty] | ​the free chlorine levels are high because the system had just fed st70 into the tower. Everything else all good | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2016-11-29 11:02 | Daimon A. Boccamazzo
560 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-03 08:50 | 825 |  | 8.9 | 320 | [8 empty] | 8.8 | [13 empty] | ​tower has a high free chlorine level because the system had just pumped st70 into the tower before I tested it | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-10-14 08:52 | Daimon A. Boccamazzo
561 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-02 14:14 | 765 |  | 8.4 | 200 | [8 empty] | 8.8 | [13 empty] | ​​free chlorine levels high because the system had just pumped st70 into the tower and I ended up testing it right after that | Daimon A. Boccamazzo | Not Adjusted |  | 79 | 2016-09-06 14:16 | Daimon A. Boccamazzo
562 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-26 10:16 | 661 |  | 8.6 | 225 | [8 empty] | 8.8 | [13 empty] | ​chenged st70 feeding to 30 mins every mon,wed, and Friday at 8. Instead of feeding for an hour. Seemed like too much for the tower cause my readings were above 8 after 24 hours | Daimon A. Boccamazzo | Not Adjusted |  | 84 | 2016-07-26 10:21 | Daimon A. Boccamazzo
563 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-06 09:09 | 557 |  | 8.6 | 220 | [8 empty] | 8.8 | [13 empty] | ​temperature seems kinda high. Free chlorine off the charts because it just got done feeding for and hour. St70 (Nalco chemical) and ch2o chemicals calls are hooked up but not the 3dt222 and the h-550 | Daimon A. Boccamazzo | Not Adjusted |  | 93 | 2016-06-07 09:13 | Daimon A. Boccamazzo
564 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-23 09:26 | 450 |  | 8.8 | 162 | [8 empty] | 0.1 | [13 empty] | ​controller still won't respond when touching the screen so I wasn't able to check what time the free chlorine gets pumped into the system. Strainer is still good. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-05-23 09:31 | Daimon A. Boccamazzo
565 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 10:22 | 430 |  | 8.65 | 224 | [8 empty] | 0.03 | [13 empty] | ​chemicals are here but not hooked up, still using ch2o unibrom plus. Controller not responding when you push buttons on the screen. Strainer is good | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-05-09 10:27 | Daimon A. Boccamazzo
566 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-18 07:38 | 420 |  | 7.6 | 95 | [8 empty] | 0 | [13 empty] | ​​Nalco controller is hooked up, chemicals are there but it is not operating yet | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-19 07:46 | Daimon A. Boccamazzo
567 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 14:02 | 350 | 0 | 8.1 | 210 | [8 empty] | 0 | [13 empty] | ​Tower is waiting on chem pump, chemicals and controller programming | Bob A Adams | Not Adjusted |  | 77 | 2016-03-31 14:05 | Bob A Adams
568 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-24 09:13 | 784 | 7 | 8.1 | 315 | [8 empty] | 3.1 | [13 empty] | ​posca in range. | Bob A Adams | Not Adjusted |  | 70 | 2016-03-24 09:15 | Bob A Adams
569 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-24 13:53 | 786 | 6 | 8.5 | 280 | [8 empty] | 0.8 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 708 | 2016-02-24 13:56 | Bob A Adams
570 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-11 08:31 | 842 | 8 | 8.5 | 241 | [8 empty] | 1.4 | [13 empty] | Posca in range. Cleaned sensors.​ | Bob A Adams | Not Adjusted |  |  | 2016-02-12 08:33 | Bob A Adams
571 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-09 08:19 | 838 | 8 | 8.4 | 286 | [8 empty] | 2.1 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 69.6 | 2016-02-09 08:21 | Bob A Adams
572 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-26 14:06 | 645 | 6 | 8.5 | 289 | [8 empty] | 1.2 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 70 | 2016-01-28 14:08 | Bob A Adams
573 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-19 14:39 | 564 | 6 | 8.3 | 230 | [8 empty] | 1.8 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 71.3 | 2016-01-19 14:41 | Bob A Adams
574 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-05 10:58 | 636 | 6 | 8.5 | 296 | [8 empty] | 1.6 | [13 empty] | ​cleaned Sensors. Posca in range . Calibrated conductivity and orp | Bob A Adams | Not Adjusted |  | 69.3 | 2016-01-05 11:02 | Bob A Adams
575 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:39 | 649 | 4 | 8.5 | 305 | [8 empty] | 1.2 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 72 | 2015-12-31 07:41 | Bob A Adams
576 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:26 | 615 | 4 | 8.6 | 272 | [8 empty] | 0.6 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 69 | 2015-12-31 07:31 | Bob A Adams
577 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 06:44 | 633 | 4 | 8.5 | 310 | [8 empty] | 1.3 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 73.5 | 2015-12-09 06:46 | Bob A Adams
578 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-19 14:06 | 641 | 4 | 8.6 | 286 | [8 empty] | 0.8 | [13 empty] | ​cleaned sensors and Posca in range | Bob A Adams | Not Adjusted |  | 72 | 2015-11-30 14:08 | Bob A Adams
579 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-09 14:00 | 632 | 6 | 8.6 | 255 | [8 empty] | 0.6 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 69 | 2015-11-30 14:06 | Bob A Adams
580 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-28 06:52 | 586 | 6 | 8.5 | 279 | [8 empty] | 0.8 | [14 empty] | Bob A Adams | Not Adjusted |  | 73.3 | 2015-11-03 06:54 | Bob A Adams
581 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-27 14:29 | 589 | 6 | 8.5 | 248 | [8 empty] | 0.5 | [13 empty] | ​Posca and conductivity in range | Bob A Adams | Not Adjusted |  | 72 | 2015-10-28 14:33 | Bob A Adams
582 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-05 14:27 | 612 | 6 | 8.5 | 300 | [8 empty] | 1.6 | [13 empty] | ​Posca in range. Cleaned sensors. | Bob A Adams | Not Adjusted |  | 75 | 2015-10-05 14:29 | Bob A Adams
583 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-05 06:47 | 571 | 6 | 8.5 | 67 | [8 empty] | 0 | [13 empty] | ​Bromine pump failed and was replaced. Cleaned sensors. Posca is in range. | Bob A Adams | Not Adjusted |  | 73 | 2015-10-08 06:51 | Bob A Adams
584 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-23 06:27 | 640 | 8 | 8.5 | [9 empty] | 0.6 | [13 empty] | ​posca is in range. ORP is 261 | Bob A Adams | Not Adjusted |  | 78 | 2015-09-23 06:30 | Bob A Adams
585 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-25 09:01 | 631 |  | 8.5 | [23 empty] | ​ORP = 252 TWO = 0.6 OP = 6 | mrh4 | Not Adjusted |  | 76 | 2015-09-23 09:02 | Marilyn Fick
586 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-18 09:00 | 631 |  | 8.5 | [23 empty] | ​ORP = 221 TWO = 0.2​ OP = 6 | mrh4 | Not Adjusted |  | 80 | 2015-09-23 09:01 | Marilyn Fick
587 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-11 08:59 | 635 |  | 8.5 | [23 empty] | ​ORP = 247​ TWO = 0.7 OP = 6 | mrh4 | Not Adjusted |  | 75.4 | 2015-09-23 09:00 | Marilyn Fick
588 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-04 08:58 | 656 |  | 8.4 | [23 empty] | ORP = 260 TWO = 2.4 OP = 4​ | mrh4 | Not Adjusted |  | 76.3 | 2015-09-23 08:59 | Marilyn Fick
589 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-01 08:57 | 639 |  | 8.5 | [23 empty] | ​ORP = 268 TWO = 1.5 OP = 4 POSCA 260-275 | mrh4 | Not Adjusted |  | 79.2 | 2015-09-23 08:58 | Marilyn Fick
590 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-05 08:55 | 601 |  | 8.4 | [23 empty] | ​ORP = 279 TWO = 0.8 OP = 6 | mrh4 | Not Adjusted |  | 74.2 | 2015-09-23 08:57 | Marilyn Fick
591 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-01 08:53 | 631 |  | 8.4 | [23 empty] | ​ORP = 301 TWO = 2 OP = 2 POSCA ON 10 MIN | mrh4 | Not Adjusted |  | 73.9 | 2015-09-23 08:55 | Marilyn Fick
592 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-20 08:52 | 618 |  | 8.4 | [23 empty] | ​ORP = 246​ TWO = 0.7 OP = 6 | mrh4 | Not Adjusted |  | 76 | 2015-09-23 08:53 | Marilyn Fick
593 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-20 08:44 | 618 |  | 8.4 | [23 empty] | ​ ORP - 246 TWO - .7 OP - 6 | mrh4 | Not Adjusted |  | 76 | 2015-09-21 08:52 | Jay Dahlstrom
594 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-01 08:49 | 608 |  | 8.4 | [23 empty] | ​ORP = 274 TWO = 0.5 OP = 4 | mrh4 | Not Adjusted |  | 72 | 2015-09-23 08:52 | Marilyn Fick
595 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-23 08:47 | 619 |  | 8.5 | [23 empty] | ​ORP = 272 TWO = 0.1 OP = 2 | mrh4 | Not Adjusted |  | 70.2 | 2015-09-23 08:48 | Marilyn Fick
596 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 08:45 | 622 |  | 8.5 | [23 empty] | ​ORP = 278 TWO = 0.2 OP = 6​ POSCA 250-260 ppm | mrh4 | Not Adjusted |  | 70.2 | 2015-09-23 08:47 | Marilyn Fick
597 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 08:43 | 606 |  | 8.4 | [23 empty] | ​​ORP = 274 TWO = 0.8 OP = 4 Turned on POSCA 10 | mrh4 | Not Adjusted |  | 71.5 | 2015-09-23 08:45 | Marilyn Fick
598 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-16 13:53 | 590 |  | 7.7 | [23 empty] | ​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.7 | 2015-09-21 13:53 | Jay Dahlstrom
599 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-09 08:42 | 608 |  | 8.3 | [23 empty] | ​ORP = 272 TWO = 0.6 OP = 6 | mrh4 | Not Adjusted |  | 72 | 2015-09-23 08:43 | Marilyn Fick
600 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-27 08:41 | 608 |  | 8.3 | [23 empty] | ​ORP = 280 TWO = 0.9 OP = 6 POSCA 240-250 | mrh4 | Not Adjusted |  | 72 | 2015-09-23 08:42 | Marilyn Fick
601 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-13 08:35 | 727 |  | 8.4 | [23 empty] | ​ORP = 273 TWO = 0.6 OP = 6​ POSCA 230 - 240 pms | mrh4 | Not Adjusted |  | 71.7 | 2015-09-23 08:36 | Marilyn Fick
602 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-04 08:33 | 613 |  | 8.1 | [23 empty] | ​​ORP = 158 TWO = 0 OP = 4 | mrh4 | Not Adjusted |  | 67.9 | 2015-09-23 08:34 | Marilyn Fick
603 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-03 08:32 | 639 |  | 8.1 | [23 empty] | ​ORP = 199 TWO = 0.3 OP = 6 | mrh4 | Not Adjusted |  | 70.5 | 2015-09-23 08:33 | Marilyn Fick
604 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-26 08:31 | 595 |  | 8.3 | [23 empty] | ​ORP = 200 TWO = ​0.1 OP = 8 | mrh4 | Not Adjusted |  | 67.5 | 2015-09-23 08:32 | Marilyn Fick
605 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-18 08:28 | 533 |  | 8.4 | [23 empty] | ​​ORP = 240 TWO = 0.8 OP = 8 | mrh4 | Not Adjusted |  | 68.4 | 2015-09-23 08:29 | Marilyn Fick
606 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-05 08:26 | 632 |  | 7.8 | [23 empty] | ​​​​ORP = 245 TWO = 0.9 OP = 4 | mrh4 | Not Adjusted |  | 71.7 | 2015-09-23 08:28 | Marilyn Fick
607 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-27 08:24 | 564 |  | 8.5 | [23 empty] | ORP = 245 TWO = 1.0 OP = 6 | mrh4 | Not Adjusted |  | 71.1 | 2015-09-23 08:26 | Marilyn Fick
608 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-22 08:23 | 648 |  | 8.4 | [23 empty] | ​ORP = 240 TWO = 0.6​ OP = 4 | mrh4 | Not Adjusted |  | 70.5 | 2015-09-23 08:24 | Marilyn Fick
609 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-15 08:21 | 596 |  | 8.2 | [23 empty] | ​​ORP = 268 TWO = 1.1 OP = 6 | mrh4 | Not Adjusted |  | 68.8 | 2015-09-23 08:22 | Marilyn Fick
610 | 1175 | 1175-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-05 08:11 | 606 |  | 8.2 | [23 empty] | TWO = 1.0​ OP = 6 | mrh4 | Not Adjusted |  | 72.3 | 2015-09-23 08:20 | Marilyn Fick
611 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-20 10:10 | 1519 |  |  | 282 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-10-01 10:10 | RICHARD A. JOHNSON
612 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:36 | 1953 |  |  | 142 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 66 | 2018-08-30 11:36 | RICHARD A. JOHNSON
613 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 10:43 | 694 |  |  | 254 | [8 empty] | 0.4 | [13 empty] | ​system still pretty dirty but good flow going through the loop. Tower will feed st70 later today so FC levels are okay for now. Cleaned strainer and conductivity probe. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2018-08-10 10:46 | Daimon A. Boccamazzo
614 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 07:02 | 645 |  |  | 197 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2018-07-03 07:03 | RICHARD A. JOHNSON
615 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-22 10:16 | 962 |  |  | 255 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2018-02-23 10:17 | RICHARD A. JOHNSON
616 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-28 14:00 | 311 |  |  | 192 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 65 | 2017-12-29 14:00 | RICHARD A. JOHNSON
617 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-19 10:27 | 316 |  |  | 203 | [8 empty] | 0.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2017-10-23 10:29 | RICHARD A. JOHNSON
618 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:22 | 1355 |  |  | 168 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2017-08-24 08:22 | RICHARD A. JOHNSON
619 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 07:44 | 349 |  |  | 160 | [8 empty] | 0.4 | [13 empty] | ​tested on a feed day | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2017-08-02 07:46 | RICHARD A. JOHNSON
620 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-03 12:12 | 3370 |  | 8.6 | 307 | [8 empty] | 1.1 | [13 empty] | ​​drained water out of the system so that make up water would go into the system and bring the conductivity down to at least 1800. Also cleaned the strainer, flow meter, and conductivity sensor. | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2017-01-17 12:18 | Daimon A. Boccamazzo
621 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-28 11:07 | 3366 |  | 8.5 | [9 empty] | 0.2 | [13 empty] | ​cond was way too high so I drained water so that fresh water would fill the system | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2016-11-29 11:15 | Daimon A. Boccamazzo
622 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-03 08:57 | 2800 |  | 9 | 281 | [8 empty] | 2.6 | [13 empty] | ​drained water out of the system to bring fresh water in so the conductivity would go down. I think the conductivity sensor needs to be calibrated cause it is reading 1700 and my meter read 2800. I cleaned the flow and conductivity sensor and also the str | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-10-14 09:01 | Daimon A. Boccamazzo
623 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-02 14:23 | 3368 |  | 8.6 | 300 | [8 empty] | 0.2 | [13 empty] | ​​drained water of the system so I could get some fresh water in the tower and bring the conductivity down. I cleaned the strainer, flow, and conductivity sensors. Also I pumped st70 into the system for 45 mins | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-09-06 14:26 | Daimon A. Boccamazzo
624 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-26 10:25 | 1747 |  | 8.7 | 248 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Tower feeds st70 tomorrow so the free chlorine levels should be up then. | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-07-26 10:28 | Daimon A. Boccamazzo
625 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-28 13:47 | 378 |  | 8.5 | 133 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer, flow sensor, and conductivity sensor. Changed st70 timer to mon, wed, and fri for an hour at 11am and put a timer for h-550 for 15 minutes at 9am mon-fri. Conductivity sensor needs to be calibrated, it is reading 1100 and my meter is re | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-06-28 13:56 | Daimon A. Boccamazzo
626 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-23 11:10 | 2122 |  | 8.9 | 244 | [8 empty] | 0.5 | [13 empty] | ​cleaned strainer. Need reminding on how to force bleed the tower without the controller so I can bring the conductivity down. Need update on getting this controller on and running. I don't know how to force st70 into the system without the controller bei | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-05-23 11:14 | Daimon A. Boccamazzo
627 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 08:58 | 1275 | [25 empty] | ​forced bled the tower water and forced some make up water in the system to bring the conductivity down which was 2300 when I first got there | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-12 08:59 | Daimon A. Boccamazzo
628 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 12:07 | 2244 |  | 8.89 | 232 | [8 empty] | 0.06 | [13 empty] | ​chemical loop strainer was really dirty, I cleaned it but it will need to be cleaned again in a couple of days. There was a leak on the 3dt222 porta feed cause there were fittings that were loose but they got tightened and the leak is no more | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-05-10 12:11 | Daimon A. Boccamazzo
629 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-19 09:16 | 1385 |  | 8.2 | 124 | [8 empty] | 0.1 | [13 empty] | ​Nalco controller was not on, portal feeds are there but there is no chemicals in them, cleaned piping strainer. Also drained water to bring the conductivity down and opened the make up water valve to make sure that was enough water in the tower | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-19 09:21 | Daimon A. Boccamazzo
630 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-04 11:00 | 352 | 0 | 8.4 | 190 | [8 empty] | 0 | [13 empty] | ​Added Posca and Bromine to sump | Bob A Adams | Not Adjusted |  | 60 | 2016-04-04 11:02 | Bob A Adams
631 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-01 13:38 | 894 | 0 | 8.6 | 194 | [8 empty] | 0.1 | [13 empty] | ​Nalco is in progress of installing new system. Tanks in place waiting for chemical and pumps | Bob A Adams | Not Adjusted |  | 54 | 2016-04-01 13:40 | Bob A Adams
632 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-24 10:58 | 642 | 8 | 8.4 | 238 | [8 empty] | 0.1 | [13 empty] | ​posca in range. Bromine was empty, replaced | Bob A Adams | Not Adjusted |  | 51.7 | 2016-03-24 11:02 | Bob A Adams
633 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-07 07:21 | 642 | 8 | 8.1 | 406 | [8 empty] | 1.1 | [13 empty] | ​posca in range | Bob A Adams | Not Adjusted |  | 50.1 | 2016-03-07 07:23 | Bob A Adams
634 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-09 14:40 | 654 | 8 | 8.5 | 286 | [8 empty] | 1.8 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 67.2 | 2016-02-09 14:42 | Bob A Adams
635 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-26 14:08 | 652 | 7 | 8.4 | 360 | [8 empty] | 2 | [14 empty] | Bob A Adams | Not Adjusted |  | 69.2 | 2016-01-28 14:10 | Bob A Adams
636 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-15 08:54 | 644 | 8 | 8.5 | 267 | [8 empty] | 0.8 | [13 empty] | ​Posca in range. | Bob A Adams | Not Adjusted |  | 68 | 2016-01-15 08:56 | Bob A Adams
637 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-11 06:28 | 653 | 11 | 8.5 | 170 | [8 empty] | 0.1 | [13 empty] | ​Posca in range. Cleaned sensors. | Bob A Adams | Not Adjusted |  | 67 | 2016-01-12 06:35 | Bob A Adams
638 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-05 07:08 | 640 | 12 | 8.4 | 310 | [8 empty] | 1.2 | [13 empty] | ​Posca in range. Cleaned sensors. Calibrated orp. | Bob A Adams | Not Adjusted |  | 68.1 | 2016-01-05 07:11 | Bob A Adams
639 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:31 | 642 | 6 | 8.5 | 252 | [8 empty] | 0.8 | [14 empty] | Bob A Adams | Not Adjusted |  | 70.1 | 2015-12-31 07:34 | Bob A Adams
640 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 06:50 | 653 | 6 | 8.6 | 256 | [8 empty] | 0.7 | [13 empty] | ​cleaned sensors. Posca in range. | Bob A Adams | Not Adjusted |  | 69.1 | 2015-12-09 06:53 | Bob A Adams
641 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-07 06:37 | 643 | 4 | 8.5 | 310 | [8 empty] | 1.2 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 70 | 2015-12-09 06:40 | Bob A Adams
642 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-03 14:32 | 636 | 6 | 8.5 | 320 | [8 empty] | 1.3 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 69 | 2015-12-04 14:34 | Bob A Adams
643 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-30 13:51 | 651 | 6 | 8.6 | 141 | [8 empty] | 0.2 | [13 empty] | ​Posca in range. Chlorine in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 68.9 | 2015-11-30 13:53 | Bob A Adams
644 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-12 13:51 | 650 | 6 | 8.5 | 228 | [8 empty] | 0.1 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 69.3 | 2015-11-16 13:53 | Bob A Adams
645 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-06 14:00 | 648 | 10 | 8.5 | 197 | [8 empty] | 0.1 | [13 empty] | ​​Posca in range. Cleaned sensors. Set time | Bob A Adams | Not Adjusted |  | 70.7 | 2015-11-06 14:03 | Bob A Adams
646 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-27 14:21 | 626 | 8 | 8.5 | 281 | [8 empty] | 0.7 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 68 | 2015-10-28 14:23 | Bob A Adams
647 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-06 06:42 | 648 | 8 | 8.6 | 275 | [8 empty] | 0.5 | [13 empty] | ​Posca in range. Cleaned sensors. | Bob A Adams | Not Adjusted |  | 68.5 | 2015-10-08 06:46 | Bob A Adams
648 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-28 14:03 | 649 | 6 | 8.5 | 268 | [8 empty] | 0.5 | [14 empty] | Bob A Adams | Not Adjusted |  | 68.5 | 2015-10-01 14:05 | Bob A Adams
649 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-24 13:16 | 637 |  | 8.5 | [23 empty] | ​​ORP= 280 TWO= .5 OP= 6 | mrh4 | Not Adjusted |  | 66.3 | 2015-09-24 13:17 | Cesar Escobar
650 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-24 13:12 | 654 |  | 8.2 | [23 empty] | ​​ORP= 258 TWO= .8 OP= 6 | mrh4 | Not Adjusted |  | 68 | 2015-09-24 13:13 | Cesar Escobar
651 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-21 07:05 | 667 | 4 | 8.3 | [9 empty] | 0.3 | [13 empty] | ​posca was in range. 283 orp | Bob A Adams | Not Adjusted |  | 68.3 | 2015-09-21 07:11 | Bob A Adams
652 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-20 13:31 | 647 |  | 8.5 | [23 empty] | ​​ORP= 301 TWO= 1.1 OP= 6 | mrh4 | Not Adjusted |  | 67 | 2015-09-24 13:32 | Cesar Escobar
653 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-10 13:29 | 643 |  | 8.5 | [23 empty] | ​​ORP= 279 TWO= .7 OP= 6 | mrh4 | Not Adjusted |  | 69.5 | 2015-09-24 13:31 | Cesar Escobar
654 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-05 13:28 | 641 |  | 8.7 | [23 empty] | ​​ORP= 200 TWO= .1 OP= 8 | mrh4 | Not Adjusted |  | 69.1 | 2015-09-24 13:29 | Cesar Escobar
655 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-03 13:27 | 648 |  | 8.5 | [23 empty] | ​​ORP= 269 TWO= 1.0 OP= 6 | mrh4 | Not Adjusted |  | 69 | 2015-09-24 13:28 | Cesar Escobar
656 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-02 13:26 | 651 |  | 8.5 | [23 empty] | ​​ORP= 262 TWO= .9 OP= 6 | mrh4 | Not Adjusted |  | 68 | 2015-09-24 13:27 | Cesar Escobar
657 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-12 13:24 | 635 |  | 8.5 | [23 empty] | ​ORP= 292 TWO= .9 OP= 8 | mrh4 | Not Adjusted |  | 68.2 | 2015-09-24 13:26 | Cesar Escobar
658 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-08 13:23 | 645 |  | 8.5 | [23 empty] | ​ORP= 313 TWO= 1.8 OP= 6 | mrh4 | Not Adjusted |  | 69.1 | 2015-09-24 13:24 | Cesar Escobar
659 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-29 13:22 | 646 |  | 8.5 | [23 empty] | ​​ORP= 305 TWO= 1.5 OP= 8 | mrh4 | Not Adjusted |  | 69 | 2015-09-24 13:23 | Cesar Escobar
660 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-24 13:21 | 644 |  | 8.4 | [23 empty] | ​​ORP= 281 TWO= .8 OP= 8 | mrh4 | Not Adjusted |  | 68.1 | 2015-09-24 13:22 | Cesar Escobar
661 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-23 13:20 | 648 |  | 8.6 | [23 empty] | ​ORP= 305 TWO= 1.7 OP= 6 | mrh4 | Not Adjusted |  | 68.9 | 2015-09-24 13:21 | Cesar Escobar
662 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 13:19 | 630 |  | 8.5 | [23 empty] | ​​ORP= 320 TWO= 1.3 OP= 4 | mrh4 | Not Adjusted |  | 68.8 | 2015-09-24 13:20 | Cesar Escobar
663 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 13:17 | 637 | [25 empty] | ​​ORP= 124 TWO= 0 OP= 6 | mrh4 | Not Adjusted |  | 68.4 | 2015-09-24 13:19 | Cesar Escobar
664 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-30 13:14 | 666 |  | 8.4 | [23 empty] | ​​ORP= 400 TWO= 1.4 OP= 4 POSCA 13-16 PMS | mrh4 | Not Adjusted |  | 68 | 2015-09-24 13:16 | Cesar Escobar
665 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-19 13:13 | 642 |  | 8.5 | [23 empty] | ​​ORP= 132 TWO= 0 OP= 6 | mrh4 | Not Adjusted |  | 67.9 | 2015-09-24 13:14 | Cesar Escobar
666 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-12 13:09 | 642 |  | 8.5 | [23 empty] | ​​ORP= 260 TWO= .1 OP= 6 | mrh4 | Not Adjusted |  | 70.1 | 2015-09-24 13:11 | Cesar Escobar
667 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-04 13:11 | 707 |  | 8.5 | [23 empty] | ​ORP= 168 TWO= 0 OP= 6 | mrh4 | Not Adjusted |  | 66.8 | 2015-09-24 13:12 | Cesar Escobar
668 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-26 08:39 | 649 |  | 8.6 | [23 empty] | ​​ORP= 264 TWO= .2 OP= 8 | mrh4 | Not Adjusted |  | 69 | 2015-09-24 08:40 | Cesar Escobar
669 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-20 08:38 | 642 |  | 8.6 | [23 empty] | ​​ORP= 252 TWO= .1 OP= 8 | mrh4 | Not Adjusted |  | 68.3 | 2015-09-24 08:39 | Cesar Escobar
670 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-18 08:36 | 60 |  | 8.6 | [23 empty] | ​​ORP= 350 TWO= 1.3 OP= 10 | mrh4 | Not Adjusted |  | 66.5 | 2015-09-24 08:38 | Cesar Escobar
671 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-10 08:35 | 645 |  | 8.6 | [23 empty] | ​​ORP= 254 TWO= .5 OP= 6 | mrh4 | Not Adjusted |  | 69.2 | 2015-09-24 08:36 | Cesar Escobar
672 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-06 08:34 | 650 |  | 8.5 | [23 empty] | ​​ORP= 170 TWO= .1 OP= 10 | mrh4 | Not Adjusted |  | 68.7 | 2015-09-24 08:35 | Cesar Escobar
673 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-28 08:32 | 647 |  | 8.6 | [23 empty] | ​​ORP= 245 TWO= .6 OP= 4 | mrh4 | Not Adjusted |  | 68.9 | 2015-09-24 08:34 | Cesar Escobar
674 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-23 08:31 | 649 |  | 8.6 | [23 empty] | ​OP= 8 | mrh4 | Not Adjusted |  | 68.5 | 2015-09-24 08:32 | Cesar Escobar
675 | 1168 | 1168-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-16 08:22 | 625 |  | 8.6 | [23 empty] | ​ORP= 270 TWO= .5 OP= 8 | mrh4 | Not Adjusted |  | 67.6 | 2015-09-24 08:26 | Cesar Escobar
676 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 10:24 | [26 empty] | ​tower still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2018-08-10 10:25 | Daimon A. Boccamazzo
677 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2017-09-13 13:59 | [26 empty] | ​tower is still offline. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-09-13 14:01 | Daimon A. Boccamazzo
678 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2017-05-02 08:38 | [26 empty] | ​tower is still offline. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-05-16 08:40 | Daimon A. Boccamazzo
679 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-03 11:49 | [26 empty] | ​still the same as last time I checked | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-17 11:50 | Daimon A. Boccamazzo
680 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-28 10:57 | [26 empty] | ​still offline but ready to be put back online | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-11-29 10:58 | Daimon A. Boccamazzo
681 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-03 08:46 | [26 empty] | ​​tower is still offline still but it is ready to go back online. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-10-14 08:49 | Daimon A. Boccamazzo
682 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-26 10:12 | [26 empty] | Tower is still offline. New walchem controller put in and new chemicals all reading to go when tower starts up | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-07-26 10:15 | Daimon A. Boccamazzo
683 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-06 09:06 | [26 empty] | ​old chemicals still hooked up. Cooling tower still offline for repairs, no new progress made that I could see sense the last time I was there. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-06-07 09:08 | Daimon A. Boccamazzo
684 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-23 09:22 | [26 empty] | ​tower is still offline. Looks the same as last time I checked it | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-23 09:24 | Daimon A. Boccamazzo
685 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-09 10:19 | [26 empty] | ​cooling tower still offline. Plumbers getting further on repairs | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-09 10:21 | Daimon A. Boccamazzo
686 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-18 11:28 | 420 |  | 7.6 | 95 | [8 empty] | 0 | [13 empty] | ​Nalco controller is hooked up, Chemicals are there but it is not operating yet WRONG TOWER THIS IS RR-WING--DN3 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-18 11:31 | Daimon A. Boccamazzo
687 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-18 10:23 | [26 empty] | ​tower is off for repairs | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-18 10:23 | Daimon A. Boccamazzo
688 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 13:59 | 0 | 0 | 0 | 0 | [8 empty] | 0 | [13 empty] | ​Tower is empty, power off, water off | Bob A Adams | Not Adjusted |  | 0 | 2016-03-31 14:01 | Bob A Adams
689 | 1138 | 1138-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-24 09:11 | 0 | 0 | 0 | 0 | [8 empty] | 0 | [13 empty] | ​cooling tower fan and water turned off. Drain open | Bob A Adams | Not Adjusted |  | 0 | 2016-03-24 09:12 | Bob A Adams
690 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 10:47 | [26 empty] | ​tower still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2018-03-16 10:48 | Daimon A. Boccamazzo
691 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 11:14 | [26 empty] | ​tower is offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-09-11 11:16 | Daimon A. Boccamazzo
692 | 1197 | 1197-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-03-17 13:36 | 500 | 200 | 7.6 | [9 empty] | 2 | [8 empty] | Correct | Good | Clean | Clean | Level Okay | ​​Blowdown solenoid not closing. May have debris caught in it. I recommend cleaning or replacing. | reedhea |  |  |  | 2017-03-17 13:38 | reedhea
693 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-20 07:19 | [26 empty] | ​tower is still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2017-01-26 07:22 | Daimon A. Boccamazzo
694 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-05 07:52 | [26 empty] | ​still same as I left it last time | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-12-07 07:54 | Daimon A. Boccamazzo
695 | 1197 | 1197-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 12:42 | [26 empty] | ​System not running | reedhea |  |  |  | 2016-11-09 13:42 | reedhea
696 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-18 13:58 | [26 empty] | ​tower still offline until further notice | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-10-24 14:01 | Daimon A. Boccamazzo
697 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-18 12:16 | [26 empty] | ​tower still offline. Chemicals there and new transatlantic controller there and ready to go | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-07-19 12:17 | Daimon A. Boccamazzo
698 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-02 13:19 | [26 empty] | ​tower is still off line. New Nalco controller is set up and ready to go, there is also chemicals ready to be hooked up. Just waiting to get the tower fixed and turned on | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-06-02 13:21 | Daimon A. Boccamazzo
699 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-16 13:16 | [26 empty] | ​tower is still offline | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-16 13:17 | Daimon A. Boccamazzo
700 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-08 14:13 | 0 | 0 | 0 | 0 | [8 empty] | 0 | [13 empty] | ​​tower is turned off drained | Bob A Adams | Not Adjusted |  | 0 | 2016-04-08 14:14 | Bob A Adams
701 | 1197 | 1197-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-31 11:02 | 0 | 0 | 0 | 0 | [8 empty] | 0 | [13 empty] | ​Water and power are turned off at tower. Tower is drained and drain is open. | Bob A Adams | Not Adjusted |  | 0 | 2016-04-04 11:05 | Bob A Adams
702 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-14 10:25 | 928 |  |  | 131 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-10-01 10:26 | RICHARD A. JOHNSON
703 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-25 09:25 | 837 |  |  | 166 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-07-30 09:26 | RICHARD A. JOHNSON
704 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-21 10:32 | 1886 |  |  | 227 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2018-05-31 10:33 | RICHARD A. JOHNSON
705 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-22 07:51 | 847 |  |  | 160 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-04-02 07:52 | RICHARD A. JOHNSON
706 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 08:40 | 1000 |  |  | 200 | [8 empty] | 0.2 | [13 empty] | ​levels are okay. St70 scheduled to feed later today | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2018-03-16 08:51 | Daimon A. Boccamazzo
707 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-21 12:05 | 1122 |  |  | 163 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 64 | 2017-12-04 12:07 | RICHARD A. JOHNSON
708 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 10:37 | 579 |  |  | 204 | [8 empty] | 0.2 | [13 empty] | ​nothing too alarming, needs st70 jug | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2017-09-11 10:48 | Daimon A. Boccamazzo
709 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:18 | 613 |  |  | 241 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-02 10:19 | RICHARD A. JOHNSON
710 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:26 | 603 |  | 8.6 | 305 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2017-06-19 07:28 | RICHARD A. JOHNSON
734 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-06 13:00 | 654 |  | 7.9 | [23 empty] | ​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 18.1 | 2015-09-21 13:01 | Jay Dahlstrom
735 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-02 12:56 | 606 |  | 8 | [23 empty] | TEI - 4 ppm POSCA - 8 ppm​ | mrh4 | Not Adjusted |  | 18.1 | 2015-09-21 12:56 | Jay Dahlstrom
736 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-19 12:48 | 589 |  | 8.1 | [23 empty] | ​TEI - 8 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.5 | 2015-09-21 12:49 | Jay Dahlstrom
737 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-03 10:17 | 584 |  | 8.1 | [23 empty] | ​TEI - 2 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 16.6 | 2015-09-21 10:18 | Jay Dahlstrom
738 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-25 10:10 | 624 |  | 8.1 | [23 empty] | ​TEI - 4 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 22.1 | 2015-09-21 10:11 | Jay Dahlstrom
739 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-20 09:20 | 597 |  | 8 | [23 empty] | ​​TEI - 6 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 19.1 | 2015-09-21 09:21 | Jay Dahlstrom
740 | 1150 | 1150-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-10 09:11 | 617 |  | 8.7 | [23 empty] | ​​TEI - 8 ppm POSCA - 6 ppm | mrh4 | Not Adjusted |  | 19.4 | 2015-09-21 09:12 | Jay Dahlstrom
741 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-14 10:26 | 755 |  |  | 154 | [8 empty] | 2.7 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-10-01 10:27 | RICHARD A. JOHNSON
742 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-26 09:28 | 753 |  |  | 163 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 79 | 2018-07-30 09:29 | RICHARD A. JOHNSON
743 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-21 10:31 | 767 |  |  | 263 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-05-31 10:31 | RICHARD A. JOHNSON
744 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 08:35 | 690 |  |  | 245 | [8 empty] | 0.3 | [13 empty] | ​manually fed st70 into the system for 30mins to bring the FC levels up. No flow in system cause tower is on winter mode | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2018-03-16 08:37 | Daimon A. Boccamazzo
745 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-30 13:19 | 662 |  |  | 181 | [8 empty] | 0.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-02-01 13:20 | RICHARD A. JOHNSON
746 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-21 12:04 | 750 |  |  | 197 | [8 empty] | 0.2 | [13 empty] | ​ | RICHARD A. JOHNSON | Not Adjusted |  | 63 | 2017-12-04 12:05 | RICHARD A. JOHNSON
747 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 10:24 | 846 |  |  | 183 | [8 empty] | 0.1 | [13 empty] | ​FC was a little low so I fed st70 for 5 minutes to bring the levels up until the next feeding | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2017-09-11 10:36 | Daimon A. Boccamazzo
748 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:16 | 800 |  |  | 254 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 76 | 2017-08-02 10:17 | RICHARD A. JOHNSON
749 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-07-12 11:00 | 770 | 101 | 8.2 |  | 180 | 175 | 150 | 4 | 5 | 8 | 2 | 5 | 0.6 | 0.02 | 0.05 | 1000 | 10653 | 79500 | 12 | 0 | 0 | Correct | Good | Clean | Clean | Level Okay | ​System looked great! NGG not yet connected, having issues with address provided | reedhea |  |  |  | 2017-07-12 11:13 | reedhea
750 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:14 | 1151 |  | 8.5 | 187 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 65 | 2017-06-19 07:16 | RICHARD A. JOHNSON
751 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-10 12:19 | 630 | 105 | 8.2 |  | 75 | 110 | [6 empty] | 0.02 |  |  |  | 9701.6 | 72400 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​Blowdown meter is read in gallons. ST70 feed was changed to 8AM, M/W/F. H550 feed was changed to 8AM Thurs | reedhea |  |  |  | 2017-05-10 12:21 | reedhea
752 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-18 13:31 | 667 |  | 8.5 | 265 | [8 empty] | 0.2 | [13 empty] | ​st70 scheduled to feed later in the day | Daimon A. Boccamazzo | Not Adjusted |  | 71 | 2017-01-25 13:34 | Daimon A. Boccamazzo
753 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-01 13:25 | 665 |  | 8.5 | 202 | [8 empty] | 0.2 | [13 empty] | ​everything is all good, st70 schedule to fed on Friday | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-12-01 13:28 | Daimon A. Boccamazzo
754 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 15:41 | 650 | 100 | 8.6 | [9 empty] | 0.01 |  |  |  | 71200 |  |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​​ | reedhea |  |  |  | 2016-11-09 15:55 | reedhea
755 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-14 13:22 | 739 |  | 8.5 | 161 | [8 empty] | 0.2 | [13 empty] | ​found two valves that were shut. Cleaned the strainer and the conductivity sensor | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-10-24 13:25 | Daimon A. Boccamazzo
947 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-22 08:50 | 705 | 143.7 | 9.1 | [9 empty] | 0.87 | [14 empty] | mrh4 | Not Adjusted |  |  | 2015-09-22 08:59 | mrh4
948 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-26 16:44 | 659 | 167 | 8.4 |  | 230 | 224 |  | 0.26 | 5.3 | 6.7 | 0.88 | 0.2 | 0.03 | 0.064 | 0.84 |  | 897398 | 2954 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 16:46 | jrojas92
949 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-07-16 13:24 | 714 | 153 | 8.6 |  | 220 | 218 |  | 0 | 5.5 | 8.4 | 0.79 | 0.2 | 4.76 | 0.0722 | 0.59 |  | 895125 | 2294 |  |  |  |  | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-08-18 13:30 | jrojas92
950 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-22 17:34 | 620 | 151 | 8.4 |  | 180 | 186 |  | 0 | 5.1 | 5.3 | 0.82 | 0.2 | 0.02 | 0.127 | 1.22 |  | 897130 | 1824 |  |  |  | Correct | Good | Clean | Clean | Needs Filling | ​Out of ST70 | jrojas92 |  |  |  | 2015-11-14 17:36 | jrojas92
951 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-21 18:24 | 555 | 163 | 8.53 |  | 200 | 172 |  | 0.47 | 3.9 | 7.8 | 0.97 | 0.9 | 1.58 | 0.132 | 0.77 |  | 897130 | 1692 | [7 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:27 | jrojas92
952 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 13:57 | 397 | 127.1 | 8.7 | [9 empty] | 1 | [13 empty] | Fahrenheit​ | mrh4 | Not Adjusted |  | 56.2 | 2015-09-21 13:58 | Jay Dahlstrom
953 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-13 13:33 | 379 | 132.1 | 8.7 | [9 empty] | 0.33 | [13 empty] | ​Fahrenheit | mrh4 | Not Adjusted |  | 55.9 | 2015-09-21 13:34 | Jay Dahlstrom
954 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-04-08 19:01 | 343 | 171 | 7.9 |  | 100 | 98 |  | 0.4 | 4.7 | 0 | 1.81 | 0.6 | 0.47 | 0.0725 | 0.58 |  | 896996 | 1692 | [7 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 19:03 | jrojas92
955 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-06 12:59 | 381 | 139.7 | 8.7 | [9 empty] | 0.37 | [13 empty] | Fahrenheit​ | mrh4 | Not Adjusted |  | 54.2 | 2015-09-21 13:00 | Jay Dahlstrom
956 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-19 12:46 | 392 | 134.4 | 8.7 | [9 empty] | 0.02 | [13 empty] | ​​Fahrenheit | mrh4 | Not Adjusted |  | 54 | 2015-09-21 12:46 | Jay Dahlstrom
957 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-23 09:24 | 265 | 136.5 | 8.5 | [9 empty] | 0.2 | [13 empty] | ​Farhenheit | mrh4 | Not Adjusted |  | 52.2 | 2015-09-21 09:27 | Jay Dahlstrom
756 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-08 13:09 | 659 |  | 8.8 | 150 | [8 empty] | 0.2 | [13 empty] | ​cleaned strainer, st70 is scheduled to feed everyday at ten for thirty minutes and I have tested the tower at eight | Daimon A. Boccamazzo | Not Adjusted |  | 67 | 2016-09-08 13:13 | Daimon A. Boccamazzo
757 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-04 10:30 | 1173 |  | 8.9 | 172 | [8 empty] | 0.1 | [13 empty] | ​everything looked good besides the no flow alarm. Tower looks good as well | Daimon A. Boccamazzo | Not Adjusted |  | 78 | 2016-08-08 10:34 | Daimon A. Boccamazzo
758 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-30 10:46 | 601 | 95 | 8 | 99 | [8 empty] | 0.75 |  |  | 200000 | [10 empty] | ​​test | Jay Dahlstrom | Not Adjusted |  |  | 2016-06-30 10:49 | Jay Dahlstrom
759 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-01 14:49 | 632 |  | 8.7 | 130 | [8 empty] | 0.2 | [13 empty] | ​relay 4 feeds everyday at 10am for 30 minutes. Just need to find out if that relay is for the st70 or th h-550 and why there is only one chemical on scheduled feeding. Checked tower and everything looks good. | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-06-01 14:52 | Daimon A. Boccamazzo
760 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-18 23:15 | 705 | 131 | 8.5 |  | 250 | 270 |  |  | 2.3 | 5 | 0.18 | 0 | 0.05 | 0.308 | 0.53 |  | 5989.8 | 44700 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​ | jrojas92 |  |  |  | 2016-06-06 23:18 | jrojas92
761 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-13 12:28 | 570 |  | 8.1 | 248 | [8 empty] | 0.25 | [13 empty] | ​cleaned strainer out. Need to get a bucket up here for the system. Flow meter isn't showing alarms but the meter itself looks like there is little to no flow at all checked tower, no leaks tower all good | Daimon A. Boccamazzo | Not Adjusted |  | 78 | 2016-05-13 12:31 | Daimon A. Boccamazzo
762 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 11:27 | 769 |  | 8.4 | 288 | [8 empty] | 0 | [13 empty] | ​could not clean chemical loop strainer cause it was on way too tight. Alarm for no flow. Saw that one of the valves on the chemical loop was half way shut. Also I noticed that all three chemical pumps were turned up to 100 so I adjusted them down to 60. | Daimon A. Boccamazzo | Down | 60 | 67 | 2016-04-29 11:33 | Daimon A. Boccamazzo
763 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-25 21:21 | 816 | 121 | 8.5 |  | 250 | 290 |  | 0.93 | 2.6 | 1.9 | 0.32 | 0 | 0.27 | 0.444 | 2.75 |  | 5527.902 | 41253 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 21:23 | jrojas92
764 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-07 14:18 | 349 | 102 | 8.3 | 214 | [8 empty] | 0.3 | [13 empty] | ​turned on st70 20 minutes | Bob A Adams | Not Adjusted |  | 83 | 2016-04-07 14:21 | Bob A Adams
765 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-25 17:58 | 306 | 106 | 7.8 |  | 120 | 118 |  | 1.38 | 2.9 | 3.4 | 0.54 | 0 | 0.06 | 0.7831 | 2.85 |  | 5483.548 | 40922 |  |  |  | Correct | Good | Clean | Clean | Level Okay | Tower not running. ST70 tubing filled with white solids. | jrojas92 |  |  |  | 2016-05-02 18:03 | jrojas92
766 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 06:37 | 307 | 87.5 | 8.4 | 213 | [8 empty] | 0.1 | [13 empty] | ​tower was not running | Bob A Adams | Not Adjusted |  | 70 | 2016-03-29 06:41 | Bob A Adams
767 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-22 07:55 | 274 | 94.2 | 7.8 | 247 | [8 empty] | 0 | [14 empty] | Bob A Adams | Not Adjusted |  | 56.8 | 2016-03-23 07:56 | Bob A Adams
768 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-16 11:15 | 743 | 123.6 | 8.3 | 201 | [8 empty] | 0.2 | [13 empty] | ​not flowing | Bob A Adams | Not Adjusted |  | 68.9 | 2016-03-16 11:17 | Bob A Adams
769 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-22 11:39 | 698 | 104 | 8.3 | 220 | [8 empty] | 0.3 | [13 empty] | ​tower was not running | Bob A Adams | Not Adjusted |  | 67.3 | 2016-02-22 11:41 | Bob A Adams
770 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-12 14:23 | 675 | 109 | 8.5 | 289 | [8 empty] | 1.2 | [13 empty] | ​ | Bob A Adams | Not Adjusted |  | 65.8 | 2016-02-12 14:25 | Bob A Adams
771 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-05 10:41 | 690 | 99.1 | 8.3 | 170 | [8 empty] | 0.2 | [13 empty] | ​tested in no flow | Bob A Adams | Not Adjusted |  | 70.3 | 2016-02-05 10:43 | Bob A Adams
772 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-31 12:55 | 650 | 94.1 | 8.3 | 153 | [8 empty] | 0.1 | [14 empty] | Bob A Adams | Not Adjusted |  | 72 | 2015-12-31 13:01 | Bob A Adams
773 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 09:35 | 671 | 106.1 | 9.3 | 256 | [8 empty] | 1.5 | [14 empty] | mrh4 | Not Adjusted |  | 70.1 | 2015-12-14 09:54 | mrh4
774 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 14:16 | 641 | 143 | 8.3 |  | 210 | 264 |  | 0 | 3.8 | 1.5 | 0.54 | 0 | 0.15 | 0.6413 | 7.53 |  | 5136.756 | 38334 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-12-21 14:20 | jrojas92
775 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-09 11:25 | 654 | 101 | 9.24 | 101 | [8 empty] | 0.5 | [13 empty] | ​​ | mrh4 | Not Adjusted |  | 67.4 | 2015-11-24 11:27 | mrh4
776 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-02 14:45 | 682 | 108.3 | 9.4 | [9 empty] | 2 | [13 empty] | ​H 550 down to 8 gallons | mrh4 | Not Adjusted |  | 68.4 | 2015-11-02 14:47 | mrh4
777 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-30 14:53 | 682 | 133 | 8.5 |  | 230 | 288 |  | 0.83 | 2.1 | 1.8 | 0.31 | 0 | 0.02 |  | 1.5 |  | 5051.8 | 37700 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 14:57 | jrojas92
778 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-21 | 691 | 109.9 | 9.2 | 171 | [8 empty] | 0 | [13 empty] | ​slug fed biocides | mrh4 | Not Adjusted |  | 68.8 | 2015-10-26 09:41 | mrh4
779 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-28 18:26 | 676 | 224 | 8.2 |  | 230 | 270 |  | 0.04 | 5.7 | 10.3 | 1.21 | 0.5 | 0.83 | 0.0886 | 0.3 |  | 4609.6 | 34400 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-09-30 18:32 | jrojas92
780 | 5980 | 5980-Cooling_Tower-UW | Cooling Tower | UW | 2015-09-22 11:28 | 663 | 127.9 | 9.2 | [9 empty] | 0.67 | [14 empty] | mrh4 | Not Adjusted |  |  | 2015-09-22 11:33 | mrh4
781 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-08-24 16:37 | 623 | 130 | 8.5 |  | 230 | 244 |  | 0.34 | 3.32 | 2.7 | 0.17 | 0.4 | 1.95 | 0.0998 | 10.4 |  | 3778.8 | 28200 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 16:40 | jrojas92
782 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-07-16 13:06 | 651 | 121 | 8.5 |  | 230 | 258 |  | 0.12 | 2.6 | 1.7 | 0.13 | 0.3 | 0.59 | 0.0829 | 0.11 |  |  | 1965 |  |  |  |  | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-08-18 13:15 | jrojas92
783 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-06-22 17:27 | 1044 | 112 | 8.5 |  | 240 | 378 |  | 0.82 | 1.3 | 0.1 | 0.03 | 0.2 | 0.03 | 0.0772 | 0.13 |  | 549.4 | 4100 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 17:29 | jrojas92
784 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-05-21 18:19 | 1142 | 6 | 8.5 |  | 250 | 394 |  | 0.08 | 0.2 | 0 | 0.05 | 1 | 0.04 | 0.0959 | 0.29 |  | 187.6 | 1400 | [7 empty] | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 18:22 | jrojas92
785 | 5980 | 5980-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-04-08 18:56 | 975 | 5.5 | 8.1 |  | 190 | 344 |  | 0.18 | 0.82 | 8.7 | 0.17 | 0 | 0.05 | 0.203 | 8.9 |  | 187.6 | 1400 | [7 empty] | Needs Filling |  | jrojas92 |  |  |  | 2015-11-14 18:58 | jrojas92
786 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 11:07 | 3090 |  |  | 201 | [8 empty] | 0 | [13 empty] | ​need to get circa pump on system ASAP. Can't fed st70 cause system has no flow. Cleaned strainer, conductivity probe, and flow meter. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2018-08-10 11:10 | Daimon A. Boccamazzo
787 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 13:12 | 1545 |  |  | 151 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 72 | 2018-06-29 13:14 | RICHARD A. JOHNSON
788 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-17 13:28 | 1167 |  | 9.1 | 144 | [8 empty] | 0.5 | [13 empty] | ​still very little flow like always. Fed st70 for 30 mins to bring the levels up | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2017-01-17 13:29 | Daimon A. Boccamazzo
789 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-07 10:08 | 1181 |  | 9.4 | 174 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, conductivity sensor, and flow sensors. Free chlorine low cause there is no flow so the st70 didn't feed. After I cleaned the sensor there was enough flow that I was able to pump sone st70 into the tower | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-10-14 10:13 | Daimon A. Boccamazzo
790 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-07 07:01 | 1811 |  | 8.7 | 156 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Opened up the drain valve so fresh could be brought into the system to bring the conductivity down | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-09-08 07:04 | Daimon A. Boccamazzo
791 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-03 09:09 | 2099 |  | 8.6 | 177 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer, conductivity sensor and flow sensor. I opened up the bleed valve to drain some of the water out so the conductivity would go down, I got it down to 1100 and then put the st70 on for 30 mins to bring the free chlorine levels up. Really n | Daimon A. Boccamazzo | Not Adjusted |  | 78 | 2016-08-04 09:14 | Daimon A. Boccamazzo
792 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-06 08:41 | 1647 |  | 8.9 | 124 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, flow sensor, conductivity sensor. Tried to bleed some water so I could get some fresh water in the tower so the conductivity could drop. I also pumped st70 in the system for about 30-45 minutes. | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-07-08 08:45 | Daimon A. Boccamazzo
793 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-31 13:08 | 860 |  | 8.3 | 196 | [8 empty] | 0 | [13 empty] | ​consistent no flow alarms affecting the system and the chemical treatment. Need booster pump on the tower asap. Also need to get spicket fixed so I can turn the valves on so the system can try and feed some chemical into the tower | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-05-31 13:12 | Daimon A. Boccamazzo
794 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-22 23:55 | 1050 | 116 | 8.6 |  | 390 | 396 |  |  | 0.8 | 0 | 2.38 | 0 | 0 | 0.059 | 0.11 |  | 26766 | 2426 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​No flow, dirty water. Manually BD until conductivity of 700. | jrojas92 |  |  |  | 2016-06-06 23:59 | jrojas92
795 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 07:14 | 1082 |  | 8.8 | 223 | [8 empty] | 0 | [13 empty] | ​cleaned strainer, will definitely need to be cleaned next time around. Relay 4 feeds every day for 19 minutes at 12pm and relay 5 pumps every day for 5 minutes at 5pm. should probably be changed. Need booster pump on this tower cause I'm getting consiste | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-05-13 07:19 | Daimon A. Boccamazzo
796 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-28 22:33 | 994 | 242 | 8.6 |  | 360 | 394 |  | 0.23 | 2.8 | 6.2 | 5.94 | 0.6 | 0 | 0.268 | 0.17 |  | 26088 | 2424 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 22:37 | jrojas92
797 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-28 11:40 | [26 empty] | ​alarms for no flow and high conductivity, saw that the taser pump was almost all the way up to 100 and adjusted it down to 60 also I cleaned out the chemical loop filter (it was pretty clogged and dirt). Need to get a booster pump on the tower Asa's to h | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-28 11:43 | Daimon A. Boccamazzo
798 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-25 07:03 | [26 empty] | ​alarms for no flow, and high conductivity, Don needs to get a booster pump in here asap to help the flow of the entire tower and chemical system. Also need to get a bucket in the mech room for water messes | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-26 07:08 | Daimon A. Boccamazzo
799 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-15 14:35 | 615 | 158 | 7.9 | [9 empty] | 4.9 | [13 empty] | ​once I got to the tower and tried to take a sample I noticed that there was no water coming out. Then I icsolated the catch screen cup and cleaned it out and once I did that and put it back on, then the water started running. Also when I got there I noti | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-15 14:42 | Daimon A. Boccamazzo
800 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-14 14:47 | 650 | 17.1 | 7.5 | 330 | [8 empty] | 0 | [13 empty] | ​​cleaned out screen and noticed that after putting it back on and turning the valves on it almost immediately got a bunch of gunk in it. Also was not getting very much flow at all even after cleaning the flow sensor | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-14 14:55 | Daimon A. Boccamazzo
801 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-06 11:57 | 716 | 250 | 8.4 | 190 | [8 empty] | 0 | [13 empty] | ​​no flow. Tower needs booster pump | Bob A Adams | Not Adjusted |  | 78 | 2016-04-06 11:59 | Bob A Adams
802 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-29 20:31 | 787 | 9 | 8.3 |  | 180 | 160 |  | 1.18 | 1.5 | 0.4 | 3.12 | 0.4 | 0 | 0.454 | 0.43 |  | 85675 | 2423 |  |  |  | Correct |  | Clean | Clean | Level Okay | ​Dirty water. | jrojas92 |  |  |  | 2016-06-06 20:36 | jrojas92
803 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 08:23 | 735 | 250 | 8.4 | 290 | [8 empty] | 0 | [13 empty] | ​Trasar read too high | Bob A Adams | Not Adjusted |  | 75 | 2016-03-25 08:27 | Bob A Adams
804 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 10:33 | 720 | 183.5 | 8.3 | 291 | [8 empty] | 0.4 | [14 empty] | Bob A Adams | Not Adjusted |  | 72 | 2016-03-10 10:34 | Bob A Adams
805 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 14:06 | 605 | 250 | 7.5 | 316 | [8 empty] | 0 | [13 empty] | ​TRASAR only read Hi Conc. Water is still not flowing. Reported problems to Nalco Beth S. | Bob A Adams | Not Adjusted |  | 73.5 | 2016-02-08 14:10 | Bob A Adams
806 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-25 13:50 | 721 |  | 7.1 | 225 | [8 empty] | 0 | [13 empty] | ​​Trasar read Hi conc. Still no flow through chemical loop even though tower is running. | Bob A Adams | Not Adjusted |  | 72.7 | 2016-01-25 13:53 | Bob A Adams
807 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-06 13:48 | 687 | 151 | 8.5 | 200 | [8 empty] | 0.3 | [13 empty] | ​still having flow issue. Cleaned strainer and flow probe. | Bob A Adams | Not Adjusted |  | 68 | 2016-01-06 13:50 | Bob A Adams
808 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-14 07:51 | 602 | 8 | 8.4 | 289 | [8 empty] | 1.2 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 87 | 2015-12-31 07:54 | Bob A Adams
809 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 14:11 | 82 | 44.8 | 8.8 |  | 40 | 38 |  | 0.3 | 1.4 | 0 | 0.41 | 0.6 | 0.77 | 0.0664 | 0.04 | [6 empty] | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-12-22 14:13 | jrojas92
810 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-14 15:31 | 674 | 324 | 8.4 |  | 190 | 200 |  | 0.19 | 8.1 | 13.3 | 4.7 | 1.3 | 0.01 | 0.0501 | 0.09 | [6 empty] | Correct | Good | Clean | Clean |  | ​​Only 2 gal of 3DT222 left. | jrojas92 |  |  |  | 2015-11-14 15:33 | jrojas92
811 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-20 07:45 | 739 | 399 | 8.6 | 150 | [8 empty] | 0.1 | [14 empty] | Bob A Adams | Not Adjusted |  | 78 | 2015-10-26 07:48 | Bob A Adams
812 | 1106 | 1106-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-12 08:22 | 582 | 399 | 8.5 | 158 | [8 empty] | 0.4 | [14 empty] | Bob A Adams | Not Adjusted |  | 78.9 | 2015-10-26 08:24 | Bob A Adams
813 | 1106 | 1106-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-29 19:13 | 657 | 401 | 8.5 |  | 200 | 208 |  | 0 | 9.6 | 15.9 | 4.8 | 1.7 | 0.01 | 0.0731 | 0.16 | [6 empty] | Correct | Good | Clean | Clean | Level Okay | ​There was fouling/scaling of the fluorometer that was causing it to read lower Trasar level than it actually is. Tried cleaning with pipe brush, but did not help by much. | jrojas92 |  |  |  | 2015-09-30 19:19 | jrojas92
814 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:41 | 109 |  |  | 146 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 74 | 2018-08-30 11:42 | RICHARD A. JOHNSON
815 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 11:10 | 124 |  |  | 166 | [8 empty] | 0.2 | [13 empty] | ​FC levels are okay for now, tower will feed st70 tomorrow. Need to figure out how to stop the tower from draining water out for 2 hours. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2018-08-10 11:14 | Daimon A. Boccamazzo
816 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-28 13:17 | 64 |  |  | 162 | [8 empty] | 0 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 65 | 2018-06-29 13:20 | RICHARD A. JOHNSON
817 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-25 13:28 | 71 |  |  | 134 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 64 | 2018-04-30 13:29 | RICHARD A. JOHNSON
818 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-21 10:08 | 111 |  |  | 207 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 47 | 2018-02-23 10:09 | RICHARD A. JOHNSON
819 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-27 13:52 | 105 |  |  | 197 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 52 | 2017-12-29 13:54 | RICHARD A. JOHNSON
820 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-19 10:39 | 110 |  |  | 179 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2017-10-23 10:40 | RICHARD A. JOHNSON
821 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:25 | 130 |  |  | 220 | [8 empty] | 0.6 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2017-08-24 08:27 | RICHARD A. JOHNSON
822 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:22 | 131 |  |  | 251 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 75 | 2017-08-02 10:23 | RICHARD A. JOHNSON
823 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-18 13:10 | 187 |  | 9.5 | 164 | [8 empty] | 0.4 | [13 empty] | ​everything is as usual. Starting to see a increase in the chlorine levels in a good way | Daimon A. Boccamazzo | Not Adjusted |  | 55 | 2017-01-25 13:13 | Daimon A. Boccamazzo
824 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-07 10:15 | 672 |  | 9 | 176 | [8 empty] | 0.1 | [13 empty] | ​no flow alarm. Strainer is all good | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2016-10-14 10:16 | Daimon A. Boccamazzo
825 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-07 07:05 | 328 |  | 8.9 | 148 | [8 empty] | 0.5 | [13 empty] | ​cleaned strainer, flow and conductivity sensors. Conductivity still a little bit low but there are no alarms for it. But everything else looks good. | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2016-09-08 07:07 | Daimon A. Boccamazzo
826 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-04 10:09 | 294 |  | 8.9 | 151 | [8 empty] | 0 | [13 empty] | ​cleaned conductivity sensor, strainer, and flow sensor. Not sure if fans weren't running at all or if they just weren't running at the time that I got there. Bleed valve is shut but can't tell if it is leaking or not cause the drain pipe coming from the | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-08-08 10:20 | Daimon A. Boccamazzo
827 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-04 08:57 | 294 |  | 8.9 | 151 | [8 empty] | 0 | [13 empty] | ​cleaned conductivity sensor, flow sensor and strainer. Not sure if the fans to circulate the water doesn't run or if it just wasn't running when I got there to test the tower. also even though the bleed valve is shut I can't tell if the valve is leaking | Daimon A. Boccamazzo | Not Adjusted |  | 66 | 2016-08-04 09:03 | Daimon A. Boccamazzo
828 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-07 08:46 | 235 |  | 8.8 | 174 | [8 empty] | 0.1 | [13 empty] | ​chemicals are there but not hooked. One of the pumps is trying to run but it is not hooked up to any kind of chemical and stops because of that. Using ch2o chemical on the other pump. Cleaned strainer, flow sensor, and conductivity sensor | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-07-08 08:50 | Daimon A. Boccamazzo
829 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-31 13:13 | 160 |  | 8.6 | 192 | [8 empty] | 0.1 | [13 empty] | ​Robert from Nalco is finishing up the new controller install for the tower and I am sure that's why all the readings I got were pretty low. Need to get chemicals up here asap so they can be hooked up and the tower can start feeding chemical into the syst | Daimon A. Boccamazzo | Not Adjusted |  | 71 | 2016-05-31 13:16 | Daimon A. Boccamazzo
830 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 13:10 | 293 |  | 8.6 | 269 | [8 empty] | 1.4 | [13 empty] | ​low alarm on cooling tower controller, output timeout on orp/ph controller. Old walchem controller not sure how to use it. Need bucket of ch2o posca up here | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-05-12 13:14 | Daimon A. Boccamazzo
831 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 08:14 | 88 |  | 6.5 | 330 | [8 empty] | 0.1 | [13 empty] | ​still has old Walchem controllers. Showing low conductivity alarm also showing output timeout alarm. Not sure how to work the Walchem controls, would like to be taught asap in case I run into problems like this again | Daimon A. Boccamazzo | Not Adjusted |  | 56 | 2016-04-29 08:18 | Daimon A. Boccamazzo
832 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-24 13:50 | 620 | 8 | 8.4 | 203 | [8 empty] | 0.3 | [14 empty] | Bob A Adams | Not Adjusted |  | 88 | 2016-02-24 13:52 | Bob A Adams
833 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-08 11:27 | 390 | 4 | 8.3 | 118 | [8 empty] | 0 | [13 empty] | ​Posca in range. can't keep bromine primed in cold temperatures. Bleed solenoid had debri in it letting water drip out lowering conductivity. | Bob A Adams | Not Adjusted |  | 85 | 2016-02-08 11:31 | Bob A Adams
834 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-25 13:48 | 691 | 6 | 8.6 | 163 | [8 empty] | 0 | [13 empty] | ​Posca in range. Bromine pump lost prime due to cold weather. | Bob A Adams | Not Adjusted |  | 77 | 2016-01-25 13:49 | Bob A Adams
835 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-04 14:28 | 650 | 4 | 8.5 | 112 | [8 empty] | 0 | [13 empty] | ​Posca in range. Bromine continues to stop pumping due to the chemical being too cold. | Bob A Adams | Not Adjusted |  | 59 | 2015-12-04 14:32 | Bob A Adams
836 | 1112 | 1112-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-09 08:11 | 1100 | 4 | 8.7 | 350 | [8 empty] | 2 | [13 empty] | ​Posca in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 76 | 2015-10-26 08:16 | Bob A Adams
837 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 10:59 | 1891 |  |  | 460 | [8 empty] | 8.8 | [13 empty] | ​everything is so high because Tuesday I put three bottles of bleach in the tower | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2017-09-11 11:05 | Daimon A. Boccamazzo
838 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:20 | 1140 |  |  | 246 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 73 | 2017-08-02 10:21 | RICHARD A. JOHNSON
839 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:04 | 774 |  | 9 | 570 | [8 empty] | 8.8 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 54 | 2017-06-19 07:07 | RICHARD A. JOHNSON
840 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-20 14:41 | 3786 |  | 9.1 | 250 | [8 empty] | 0.2 | [13 empty] | ​not cycling water through due to cold weather. Poured one bottle of bleach in to bring the FC levels up | Daimon A. Boccamazzo | Not Adjusted |  | 51 | 2017-01-25 14:45 | Daimon A. Boccamazzo
841 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-01 13:34 | 2950 |  | 9 | 230 | [8 empty] | 2.2 | [13 empty] | ​there was bleach left over from my lasting testing and I think that's why the conductivity was so high | Daimon A. Boccamazzo | Not Adjusted |  | 45 | 2016-12-01 13:37 | Daimon A. Boccamazzo
842 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-18 13:42 | 1996 |  | 9 | 163 | [8 empty] | 0.1 | [13 empty] | ​poured tree bottles of bleach into the tower to bring the free chlorine levels up | Daimon A. Boccamazzo | Not Adjusted |  | 51 | 2016-10-24 13:47 | Daimon A. Boccamazzo
843 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-08 13:17 | 1280 |  | 8.6 | 165 | [8 empty] | 0.3 | [13 empty] | ​put 2.5 bottles of bleach into the tower to bring the free chlorine levels up | Daimon A. Boccamazzo | Not Adjusted |  | 58 | 2016-09-08 13:18 | Daimon A. Boccamazzo
844 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-07-18 10:29 | 1156 |  | 8.9 | 134 | [8 empty] | 0.1 | [13 empty] | ​dumped two bottles of bleach into the tower to bring the free chlorine levels up | Daimon A. Boccamazzo | Not Adjusted |  | 62 | 2016-07-18 10:31 | Daimon A. Boccamazzo
845 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-16 10:49 | 1716 |  | 9.1 | 625 | [8 empty] | 1.17 | [13 empty] | ​will definitely need 2 bottles of bleach next time around | Daimon A. Boccamazzo | Not Adjusted |  | 53 | 2016-05-16 10:50 | Daimon A. Boccamazzo
846 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-13 07:53 | [12 empty] | 8.8 | [13 empty] | ​levels are above 8 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-13 07:54 | Daimon A. Boccamazzo
847 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-12 08:50 | [12 empty] | 0.04 | [13 empty] | ​poured three bottles of bleach in the tower. Let pumps run for a little bit and then tested again and got .05 and then grabbed another sample and got .2. Reason why the second test was so low was cause we had poured three bottles of bleach in the system. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-12 08:55 | Daimon A. Boccamazzo
848 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-08 14:09 | 162 | 0 | 8.9 | 280 | [8 empty] | 0 | [14 empty] | Bob A Adams | Not Adjusted |  | 58 | 2016-04-08 14:10 | Bob A Adams
849 | 1345 | 1345-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-28 06:49 | 140 | 0 | 8.8 | 233 | [8 empty] | 0.1 | [13 empty] | ​no chemical system | Bob A Adams | Not Adjusted |  | 53 | 2016-03-29 06:51 | Bob A Adams
850 | 4057 | 4057-Condenser_Water-UW | Condenser Water | UW | 2015-12-14 07:46 | 845 | 8 | 8.5 | 242 | [8 empty] | 0.5 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 71 | 2015-12-31 07:48 | Bob A Adams
851 | 4057 | 4057-Condenser_Water-UW | Condenser Water | UW | 2015-12-11 07:12 | 817 | 8 | 8.5 | 232 | [8 empty] | 0.3 | [13 empty] | ​free chlorine in range. Posca in range | Bob A Adams | Not Adjusted |  | 70.3 | 2015-12-31 07:17 | Bob A Adams
852 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-24 10:14 | 3069 |  |  | 251 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-10-01 10:15 | RICHARD A. JOHNSON
853 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-08-23 11:40 | 3408 |  |  | 163 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-08-30 11:40 | RICHARD A. JOHNSON
854 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-31 10:59 | 2662 |  |  | 174 | [8 empty] | 0.3 | [13 empty] | ​porta feed for st70 still needs to be replaced. Y strainer on bleed valve was cleaned so system should be able to bleed some water when conductivity gets too high | Daimon A. Boccamazzo | Not Adjusted |  | 65 | 2018-08-10 11:03 | Daimon A. Boccamazzo
855 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-06-29 06:56 | 2578 |  |  | 160 | [8 empty] | 0.2 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2018-07-03 06:57 | RICHARD A. JOHNSON
856 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-04-23 13:23 | 1682 |  |  | 182 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 69 | 2018-04-30 13:24 | RICHARD A. JOHNSON
857 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-22 10:10 | 1774 |  |  | 131 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2018-02-23 10:11 | RICHARD A. JOHNSON
858 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2017-12-28 13:58 | 2171 |  |  | 221 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  |  | 2017-12-29 13:58 | RICHARD A. JOHNSON
859 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2017-10-18 10:41 | 1343 |  |  | 306 | [8 empty] | 0.5 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2017-10-23 10:42 | RICHARD A. JOHNSON
860 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-24 08:17 | 1992 |  |  | 177 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2017-08-24 08:18 | RICHARD A. JOHNSON
861 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 07:33 | 1631 |  |  | 168 | [8 empty] | 0.2 | [13 empty] | ​tested on an off day | RICHARD A. JOHNSON | Not Adjusted |  | 70 | 2017-08-02 07:35 | RICHARD A. JOHNSON
862 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-17 13:21 | 1146 |  | 8.8 | 135 | [8 empty] | 0.1 | [13 empty] | ​Free chlorine is low because it is in between feeding cycles | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2017-01-17 13:25 | Daimon A. Boccamazzo
863 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-11-29 11:45 | 2359 |  | 8.9 | 173 | [8 empty] | 0 | [13 empty] | ​blowdown was on when I got there. Adjusted st70 pump to 80 instead of 60 | Daimon A. Boccamazzo | Up | 80 | 69 | 2016-11-29 11:48 | Daimon A. Boccamazzo
864 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-06 09:21 | 2170 |  | 9.2 | 177 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer and conductivity sensor. Also fed chemical for 30 minutes | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-10-14 09:24 | Daimon A. Boccamazzo
865 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-06 14:42 | 2168 |  | 8.7 | 152 | [8 empty] | 0.2 | [13 empty] | ​cleaned strainer, flow, and conductivity sensors. Turned bleed valve on for 15mins to bring the conductivity levels down. Also found a shut valve, so I opened it and that solved the no flow alarm | Daimon A. Boccamazzo | Not Adjusted |  | 69 | 2016-09-06 14:45 | Daimon A. Boccamazzo
866 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-02 11:35 | 1755 |  | 8.8 | 147 | [8 empty] | 0.1 | [13 empty] | ​cleaned strainer and conductivity sensor. Need to find out why the bleed valve times out. when I got there the bleed valve was open but the conductivity was staying in that 1600 to almost 1800 range. | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-08-02 11:39 | Daimon A. Boccamazzo
867 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-29 08:33 | 1219 |  | 8.9 | 207 | [8 empty] | 1.2 | [13 empty] | ​st70 was pumping when I got there, didn't clean strainer cause i didn't want to disrupt the feeding chemical. Strainer, flow sensor and conductivity sensor will need to be cleaned next time around | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-07-08 08:37 | Daimon A. Boccamazzo
868 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-27 11:58 | 1332 |  | 8.9 | 180 | [8 empty] | 0.3 | [13 empty] | ​need to check the calibration for the conductivity on the controller cause it is reading 1200 and my meter is reading 1332. Reasoning for the free chlorine being low is because it has not feed st70 into the tower sense Wednesday at 1pm for 2 hours | Daimon A. Boccamazzo | Not Adjusted |  | 68 | 2016-05-27 12:04 | Daimon A. Boccamazzo
869 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-21 09:18 | [12 empty] | 0.5 | [13 empty] | ​​tested the tower just to make sure things were good and back to normal. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-23 09:20 | Daimon A. Boccamazzo
870 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-20 13:57 | 1097 | [11 empty] | 4.2 | [13 empty] | ​almost 2 hours after second reading (1:15) still above 2ppm protocol and st70 was feeding into the system as I was leaving. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-20 14:01 | Daimon A. Boccamazzo
871 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-20 13:55 | 1100 | [11 empty] | 5.1 | [13 empty] | ​3 hours after first free chlorine test (11:30) still above 2ppm | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-20 13:56 | Daimon A. Boccamazzo
872 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-20 13:46 | 1087 | [11 empty] | 8.8 | [13 empty] | ​start of the protocol at 8:30 am. Feed 2 gallons of 7341 | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-20 13:51 | Daimon A. Boccamazzo
873 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-20 09:16 | [12 empty] | 6.9 | [13 empty] | ​​well above range of protocol (2ppm for 8hrs) turned blowdown valve back to auto. | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-05-23 09:18 | Daimon A. Boccamazzo
874 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-10 14:53 | 791 |  | 8.7 | 247 | [8 empty] | 0.17 | [13 empty] | ​cleaned out chemical loop strainer. Need to check calibration on the controller for ph and orp. On the controller ph is reading 10.14 and my meter got 8.7. Orp is reading 319 and my meter got 247. | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2016-05-10 14:57 | Daimon A. Boccamazzo
875 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-25 11:20 | 680 |  | 8.2 | 230 | [8 empty] | 0.1 | [13 empty] | ​noticed when I walked up to the controller the ph was a little high it was reading 9.56. When I tested for the ph levels I got 8.2 but at the same time the ph level on the controller was reading 8.5. So I'm not sure if my ph level meter needs to be calib | Daimon A. Boccamazzo | Not Adjusted |  |  | 2016-04-25 11:31 | Daimon A. Boccamazzo
876 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-04 12:48 | 898 | 0 | 8.4 | 310 | [8 empty] | 1 | [13 empty] | ​pumped st70 into system hand fed. | Bob A Adams | Not Adjusted |  | 68 | 2016-04-04 12:51 | Bob A Adams
877 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-10 10:29 | 7299 | 0 | 8.5 | 224 | [8 empty] | 0.2 | [13 empty] | ​waiting for Nalco to turn on new system | Bob A Adams | Not Adjusted |  | 65 | 2016-03-10 10:31 | Bob A Adams
878 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-09 14:42 | 809 | 6 | 8.5 | 288 | [8 empty] | 0.8 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 72 | 2016-02-09 14:44 | Bob A Adams
879 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-28 14:14 | 830 | 8 | 8.5 | 285 | [8 empty] | 0.8 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 69 | 2016-01-28 14:15 | Bob A Adams
880 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-12 14:24 | 798 | 8 | 8.5 | 312 | [8 empty] | 1.1 | [14 empty] | Bob A Adams | Not Adjusted |  | 71 | 2016-01-12 14:25 | Bob A Adams
881 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-06 13:44 | 868 | 10 | 8.4 | 212 | [8 empty] | 0.1 | [13 empty] | ​Posca in range. Calibrated Temp. Cleaned sensors | Bob A Adams | Not Adjusted |  | 71 | 2016-01-06 13:46 | Bob A Adams
882 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-30 13:56 | 861 | 6 | 8.6 | 201 | [8 empty] | 0.4 | [13 empty] | ​Posca in range. Chlorine in range. Cleaned sensors | Bob A Adams | Not Adjusted |  | 72 | 2015-11-30 13:58 | Bob A Adams
883 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-18 06:55 | 848 | 8 | 8.5 | 292 | [8 empty] | 1.1 | [13 empty] | ​Posca in range. Cleaned sensors ​ | Bob A Adams | Not Adjusted |  | 70 | 2015-11-20 06:57 | Bob A Adams
884 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-12 14:03 | 845 | 6 | 8.6 | 299 | [8 empty] | 0.5 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 70.8 | 2015-11-16 14:06 | Bob A Adams
885 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-28 07:02 | 701 | 4 | 8.5 | 255 | [8 empty] | 1.5 | [13 empty] | ​Posca in range | Bob A Adams | Not Adjusted |  | 73 | 2015-11-03 07:04 | Bob A Adams
886 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-08 06:36 | 630 | 6 | 8.4 | 190 | [8 empty] | 0.3 | [13 empty] | ​Posca & free chlorine in range​ | Bob A Adams | Not Adjusted |  | 73 | 2015-10-12 06:39 | Bob A Adams
887 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-27 14:47 | 645 |  | 8.6 | [23 empty] | OPR - 310 TWO - .3 OP - 8​ | mrh4 | Not Adjusted |  | 68.6 | 2015-09-23 14:47 | Jay Dahlstrom
888 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-17 14:46 | 654 |  | 8.5 | [23 empty] | ​​OPR - 247 TWO - .5 OP - 6 | mrh4 | Not Adjusted |  | 69 | 2015-09-23 14:47 | Jay Dahlstrom
889 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-10 14:45 | 608 |  | 8.6 | [23 empty] | OPR - 150 TWO - .2 OP - 8​ | mrh4 | Not Adjusted |  | 67 | 2015-09-23 14:46 | Jay Dahlstrom
890 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-08-04 14:44 | 645 |  | 8.5 | [23 empty] | OPR - 199 TWO - .4 OP - 6​ | mrh4 | Not Adjusted |  | 68 | 2015-09-23 14:45 | Jay Dahlstrom
891 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-07-24 14:44 | 651 |  | 8.6 | [23 empty] | ​​OPR - 174 TWO - .4 OP - 6 | mrh4 | Not Adjusted |  | 69.2 | 2015-09-23 14:44 | Jay Dahlstrom
892 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-30 | 641 |  | 8.5 | [23 empty] | OPR - 110 TWO - 0 OP - 6​ | mrh4 | Not Adjusted |  | 69 | 2015-09-23 14:44 | Jay Dahlstrom
893 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-06-02 14:42 | 610 |  | 8.5 | [23 empty] | OPR - 120 TWO - .5 OP - 8​ | mrh4 | Not Adjusted |  | 69.2 | 2015-09-23 14:43 | Jay Dahlstrom
894 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-20 14:41 | 600 |  | 8.6 | [23 empty] | ​OPR - 120 TWO - 0 OP - 8​ | mrh4 | Not Adjusted |  | 69.9 | 2015-09-23 14:42 | Jay Dahlstrom
895 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-11 14:41 | 661 |  | 8.5 | [23 empty] | ​OPR - 232 TWO - 0 OP - 8 | mrh4 | Not Adjusted |  | 69.8 | 2015-09-23 14:41 | Jay Dahlstrom
896 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-05-06 14:40 | 641 |  | 8.5 | [23 empty] | ​OPR - 251 TWO - .6 OP - 6 | mrh4 | Not Adjusted |  | 69 | 2015-09-23 14:41 | Jay Dahlstrom
897 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-22 14:39 | 655 |  | 8.6 | [23 empty] | ​​OPR - 278 TWO - .8 OP - 6 | mrh4 | Not Adjusted |  | 68.8 | 2015-09-23 14:40 | Jay Dahlstrom
898 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-20 14:38 | 712 |  | 8.5 | [23 empty] | ​OPR - 131 TWO - 0 OP - 6 | mrh4 | Not Adjusted |  | 69.2 | 2015-09-23 14:39 | Jay Dahlstrom
899 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-04-15 13:40 | 593 |  | 7.7 | [23 empty] | ​TEI - 0 ppm POSCA - 8 ppm | mrh4 | Not Adjusted |  | 21.4 | 2015-09-21 13:40 | Jay Dahlstrom
900 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-18 14:32 | 389 |  | 9.2 | [23 empty] | ​OPR - 199 TWO - 0 OP - 4​ | mrh4 | Not Adjusted |  | 69.6 | 2015-09-23 14:33 | Jay Dahlstrom
901 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-03-17 14:31 | 628 |  | 8.5 | [23 empty] | ​​OPR - 291 TWO - .8 OP - 6 | mrh4 | Not Adjusted |  | 65 | 2015-09-23 14:32 | Jay Dahlstrom
902 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-02-07 14:30 | 600 |  | 8.6 | [23 empty] | ​​ORP - 283 TWO - .6 OP - 6 | mrh4 | Not Adjusted |  | 69.4 | 2015-09-23 14:31 | Jay Dahlstrom
903 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-26 14:29 | 677 |  | 8.2 | [23 empty] | ​​OPR - 196 TWO - .3 OP - 4 | mrh4 | Not Adjusted |  | 70 | 2015-09-23 14:30 | Jay Dahlstrom
904 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-22 14:29 | 497 |  | 8.5 | [23 empty] | ORP - 234 TWO - .4 OP - 4​ | mrh4 | Not Adjusted |  | 66.6 | 2015-09-23 14:29 | Jay Dahlstrom
905 | 4057 | 4057-Cooling_Tower-UW | Cooling Tower | UW | 2015-01-06 14:27 | 610 |  | 8.6 | [23 empty] | ​OPR - 157 TWO - 0 OP - 6 | mrh4 | Not Adjusted |  | 68.3 | 2015-09-23 14:28 | Jay Dahlstrom
906 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-09-17 10:27 | 1027 |  |  | 152 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 59 | 2018-10-01 10:28 | RICHARD A. JOHNSON
907 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-07-30 11:08 | 899 |  |  | 189 | [8 empty] | 2.3 | [13 empty] | ​Tower was feeding ST70 at time of the test | RICHARD A. JOHNSON | Not Adjusted |  | 79 | 2018-07-30 11:09 | RICHARD A. JOHNSON
908 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-05-18 10:26 | 761 |  |  | 149 | [8 empty] | 0.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 71 | 2018-05-31 10:27 | RICHARD A. JOHNSON
909 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-03-23 07:53 | 689 |  |  | 146 | [8 empty] | 1.1 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 59 | 2018-04-02 07:55 | RICHARD A. JOHNSON
910 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-02-26 08:24 | 750 |  |  | 285 | [8 empty] | 0.5 | [13 empty] | ​system is all good. Feeding st70 while I tested system | Daimon A. Boccamazzo | Not Adjusted |  | 59 | 2018-03-16 08:32 | Daimon A. Boccamazzo
911 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2018-01-30 13:18 | 577 |  |  | 228 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 58 | 2018-02-01 13:19 | RICHARD A. JOHNSON
912 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2017-11-21 12:01 | 640 |  |  | 199 | [8 empty] | 0.4 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 67 | 2017-12-04 12:03 | RICHARD A. JOHNSON
913 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-31 10:17 | 796 |  |  | 190 | [8 empty] | 0.3 | [13 empty] | ​good FC reading on off day of feeding | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2017-09-11 10:22 | Daimon A. Boccamazzo
914 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2017-08-02 10:14 | 770 |  |  | 233 | [8 empty] | 0.3 | [14 empty] | RICHARD A. JOHNSON | Not Adjusted |  | 81 | 2017-08-02 10:15 | RICHARD A. JOHNSON
915 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2017-06-19 07:10 | 858 |  | 9.21 | 220 | [8 empty] | 8.8 | [13 empty] | ​tower was feeding during test | RICHARD A. JOHNSON | Not Adjusted |  | 73 | 2017-06-19 07:13 | RICHARD A. JOHNSON
916 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2017-05-10 12:42 | 800 | 101 | 8.4 |  | 150 | 130 | [6 empty] | 0.61 |  |  |  |  | 25073.8 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​​ST70 feed changed to M/W/F, 8Am, 270min feeds, H550 changed to thu, 8am, 120min feed | reedhea |  |  |  | 2017-05-10 12:50 | reedhea
917 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2017-01-18 13:22 | 749 |  | 8.4 | 254 | [8 empty] | 0.1 | [13 empty] | ​no flow cause tower hardly runs due to low temps lately. St70 was scheduled to feed at 1:25 for 4 hours. | Daimon A. Boccamazzo | Not Adjusted |  | 70 | 2017-01-25 13:28 | Daimon A. Boccamazzo
918 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-12-01 13:21 | 684 |  | 8.3 | 198 | [8 empty] | 0.4 | [13 empty] | ​there was no flow when I got there cause the tower was not running do to the fact that there was no demand for it | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-12-01 13:24 | Daimon A. Boccamazzo
919 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-11-09 15:41 | 1710 | 130 | 7.9 | [9 empty] | 0.03 | [8 empty] | Correct | Good | Clean | Dirty | Level Okay | Controller blowdown was in manual off setting on arrival. Placed back into auto. Cleaned strainer. | reedhea |  |  |  | 2016-11-09 15:57 | reedhea
920 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-10-07 10:24 | 877 |  | 9 | 173 | [8 empty] | 0.1 | [13 empty] | ​everything is all good, no alarms. St70 was feeding when I got to the location and I didn't want to disrupt it to clean the strainer. | Daimon A. Boccamazzo | Not Adjusted |  | 73 | 2016-10-14 10:29 | Daimon A. Boccamazzo
921 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-09-07 07:12 | 895 |  | 8.6 | 163 | [8 empty] | 1.4 | [13 empty] | ​everything all good. Strainer may need to cleaned next time around but that's the only thing. | Daimon A. Boccamazzo | Not Adjusted |  | 75 | 2016-09-08 07:16 | Daimon A. Boccamazzo
922 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-08-04 10:24 | 920 |  | 8.7 | 177 | [8 empty] | 0.2 | [13 empty] | ​strainer is good, I checked the timer for st70 and it is set for 4 hours at 60% every Monday, Wednesday, and Friday. I'm not sure how to change the timer so I left the 4 hour timer feeding on there but just adjusted the pumps down to 40% until I know how | Daimon A. Boccamazzo | Not Adjusted |  | 84 | 2016-08-08 10:29 | Daimon A. Boccamazzo
923 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-06-30 08:57 | 652 | 99 | 7.5 | [8 empty] | 3.001 | 0.75 | 0.75 | [12 empty] | ​test | Jay Dahlstrom |  |  |  | 2016-06-30 08:59 | Jay Dahlstrom
924 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-06-01 09:11 | 362 |  | 8.5 | 185 | [8 empty] | 0.3 | [13 empty] | ​st70 is scheduled to pump at 1pm everyday for an hour and when I went there at 2:30 is was saying that it still had 20 mins left to pump and it said bleed valve lockout. Also the st70 pump doesn't seem to when it was saying it was feeding the chemical. | Daimon A. Boccamazzo | Not Adjusted |  | 76 | 2016-06-01 09:15 | Daimon A. Boccamazzo
925 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-05-18 23:23 | 469 | 168 | 8.4 |  | 190 | 206 |  |  | 4.1 | 10.7 | 0.77 | 0.7 | 0 | 0.084 | 0.5 |  | 897666 | 3170 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​The pump head tube for ST70 peristaltic pump needs replacing, not drawing chemical. | jrojas92 |  |  |  | 2016-06-06 23:29 | jrojas92
926 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-05-13 12:22 | 505 |  | 8.6 | 234 | [8 empty] | 0.05 | [13 empty] | ​need to get a new chemical loop strainer asap, it's falling apart. Scrubbed some of the milkyness off the chemical loop strainer enclosure. No alarms. Chemicals all good | Daimon A. Boccamazzo | Not Adjusted |  | 74 | 2016-05-13 12:27 | Daimon A. Boccamazzo
927 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-29 10:11 | 360 |  | 7.93 | 290 | [8 empty] | 0 | [13 empty] | ​chemical loop strainer is really dirty, has a white substance in it, I have a picture of it as well, there was an alarm for low conductivity. Also I noticed that the stabrex chemical pump was at 100 so I adjusted it down to 60 | Daimon A. Boccamazzo | Not Adjusted |  | 55 | 2016-04-29 10:16 | Daimon A. Boccamazzo
928 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-04-25 21:57 | 397 | 162 | 8.3 |  | 160 | 180 |  | 1.27 | 4.2 | 8 | 0.98 | 0.7 | 0 | 0.111 | 0.33 |  | 897666 | 3170 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 22:01 | jrojas92
929 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-04-06 14:20 | 276 | 135.1 | 8.2 | 232 | [8 empty] | 0.5 | [14 empty] | Bob A Adams | Not Adjusted |  | 62 | 2016-04-06 14:22 | Bob A Adams
930 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2016-03-25 19:52 | 239 | 158 | 7.9 |  | 90 | 110 |  | 0.23 | 4.5 | 8.4 | 1.95 | 0.4 | 0.17 | 0.159 | 0.55 |  | 897666 | 3170 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2016-06-06 19:58 | jrojas92
931 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-03-25 08:19 | 242 | 140.5 | 8.7 | 214 | [8 empty] | 0.1 | [13 empty] | ​calibrated cond and Orp | Bob A Adams | Not Adjusted |  | 56.2 | 2016-03-25 08:23 | Bob A Adams
932 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-22 11:36 | 306 | 152 | 8.5 | 309 | [8 empty] | 0.6 | [13 empty] | ​Cooling tower drained do to chiller issues | Bob A Adams | Not Adjusted |  | 47.7 | 2016-02-22 11:38 | Bob A Adams
933 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-12 08:34 | 600 | 169 | 8.7 | 356 | [8 empty] | 7.6 | [13 empty] | ​Bleed solenoid is turned off and conductivity is not raising too high. | Bob A Adams | Not Adjusted |  | 58.3 | 2016-02-12 08:38 | Bob A Adams
934 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-02-05 11:16 | 544 | 151.6 | 8.3 | 410 | [8 empty] | 6.8 | [13 empty] | ​calibrated conductivity | Bob A Adams | Not Adjusted |  | 57.6 | 2016-02-05 11:17 | Bob A Adams
935 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-28 14:17 | 345 | 161 | 8.6 | 333 | [8 empty] | 1.6 | [14 empty] | Bob A Adams | Not Adjusted |  | 59 | 2016-01-28 14:18 | Bob A Adams
936 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-27 14:12 | 299 | 94.4 | 8.6 | 235 | [8 empty] | 1.2 | [14 empty] | Bob A Adams | Not Adjusted |  | 57 | 2016-01-28 14:14 | Bob A Adams
937 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2016-01-15 08:57 | 267 | 162.1 | 8.5 | 165 | [8 empty] | 1.3 | [13 empty] | ​Small blow by stream. 3D Trasar is at order level | Bob A Adams | Not Adjusted |  |  | 2016-01-15 08:59 | Bob A Adams
938 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-30 14:49 | 325 | 155 | 8.3 | 177 | [8 empty] | 0 | [13 empty] | ​stabrex is empty | Bob A Adams | Not Adjusted |  | 53 | 2015-12-30 14:52 | Bob A Adams
939 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-12-08 09:25 | 603 | 132.7 | 9.3 | 324 | [8 empty] | 2.1 | [13 empty] | ​Portafeed for ST 70 is empty. Need to reorder ASAP | mrh4 | Not Adjusted |  | 60.6 | 2015-12-14 09:31 | mrh4
940 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-11-24 14:23 | 600 | 182 | 8.5 |  | 120 | 120 |  | 0.4 | 5.3 | 8.2 | 1.63 | 0.7 | 10.2 | 0.1484 | 0.87 |  | 897532 | 3170 |  |  |  | Correct | Good | Clean | Clean | Level Okay | ​ST70 chemical is low (5 gal). | jrojas92 |  |  |  | 2015-12-21 14:26 | jrojas92
941 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-09 11:22 | 593 | 122.3 | 9 | 122 | [8 empty] | 1.1 | [14 empty] | mrh4 | Not Adjusted |  | 54.1 | 2015-11-24 11:23 | mrh4
942 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-11-02 14:41 | 515 | 131.8 | 9.2 | [9 empty] | 2 | [13 empty] | ​ST 70 is down to 9 gallons | mrh4 | Not Adjusted |  | 53.1 | 2015-11-02 14:43 | mrh4
943 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-10-30 15:05 | 462 | 179 | 8.4 |  | 120 | 120 |  | 0.62 | 5.9 | 8.4 | 1.53 | 0.8 | 0.56 |  | 2.27 |  | 897532 | 3170 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-11-14 15:08 | jrojas92
944 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-21 09:31 | 423 | 121 | 9.1 | 242 | [8 empty] | 2 | [13 empty] | ​ | mrh4 | Not Adjusted |  | 54.1 | 2015-10-26 09:34 | mrh4
945 | 1420 | 1420-Cooling_Tower-UW | Cooling Tower | UW | 2015-10-16 12:00 | 272 | 257.2 | 7.7 | 301 | [8 empty] | 1 | [13 empty] | ​Restarted both cooling towers after cleaning and repairs | mrh4 | Not Adjusted |  | 73.5 | 2015-10-16 12:03 | mrh4
946 | 1420 | 1420-Cooling_Tower-NALCO | Cooling Tower | NALCO | 2015-09-24 18:39 | 650 | 161 | 8.4 |  | 270 | 214 |  | 0.39 | 5.5 | 10.2 | 0.84 | 0.8 | 0.68 | 0.0684 | 0.51 |  | 897398 | 3114 |  |  |  | Correct | Good | Clean | Clean | Level Okay |  | jrojas92 |  |  |  | 2015-09-30 18:43 | jrojas92