## query (7)
UniqueID | FacNum | LoopType | EntryGroup | Conductivity | pH | Molybdate | Nitrite | Azole | Copper | Iron | TotalBacteria | MakeupMeter | MildCopperCorrosionRate | MildSteelCorrosionRate | Leaks | Notes | DataEntryUser | SurveyDate | Created | CreatedBy
1 | 1008 | Chilled Water | NALCO | 460 | 8.1 | 5.5 | 0 |  |  | 5.1 | 100 |  |  |  |  | ​ | reedhea | 2017-03-31 09:00 | 2017-04-10 09:02 | Jay Dahlstrom
2 | 1008 | Chilled Water | NALCO | 469 | 8.4 | 34.7 | 0 | 4.2 | 0.007 | 4.81 |  | 29924.88 |  |  |  |  | jrojas92 | 2016-05-16 22:53 | 2016-06-06 22:55 | jrojas92
3 | 1008 | Chilled Water | NALCO | 470 | 8.2 | 16.3 | 0 | 5.2 | 0 | 5.13 |  | 29924.88 |  |  |  |  | jrojas92 | 2016-04-18 20:57 | 2016-06-06 21:00 | jrojas92
4 | 1008 | Chilled Water | NALCO | 466 | 8.5 | 21.6 | 0 | 3.8 | 0 | 5.33 |  | 29924.88 |  |  |  |  | jrojas92 | 2016-03-25 22:11 | 2016-04-27 22:13 | jrojas92
5 | 1008 | Chilled Water | NALCO | 476 | 8.2 | 23 | 0 | 5.4 | 0 | 4.33 |  | 29924.88 |  |  | No Leaks |  | jrojas92 | 2015-11-24 13:59 | 2015-12-21 14:01 | jrojas92
6 | 1008 | Chilled Water | NALCO | 486 | 8.2 | 34.5 | 0 | 5.7 | 0 | 4.28 |  | 29922.2 |  |  | No Leaks | ​ | jrojas92 | 2015-10-23 14:19 | 2015-11-14 14:23 | jrojas92
7 | 1008 | Chilled Water | NALCO | 479 | 8.7 | 44.9 | 0 | 5.8 | 0 | 6.2 |  | 29922.2 |  |  | No Leaks |  | jrojas92 | 2015-09-28 17:34 | 2015-09-30 17:38 | jrojas92
8 | 1008 | Chilled Water | NALCO | 479 | 8.7 | 58.8 | 0 | 6.7 | 0 | 5.93 |  | 29920.86 |  |  | No Leaks |  | jrojas92 | 2015-08-24 16:22 | 2015-11-14 16:24 | jrojas92
9 | 1008 | Chilled Water | NALCO | 486 | 8.3 | 62 | 40 | 5.5 | 0 | 5.55 |  | 29849 |  |  |  |  | jrojas92 | 2015-07-17 12:10 | 2015-08-18 12:18 | jrojas92
10 | 1008 | Chilled Water | NALCO | 482 | 8.38 | 67.5 | 0 | 5.3 | 0 | 6.68 |  | 29920.86 |  |  | No Leaks |  | jrojas92 | 2015-06-19 17:12 | 2015-11-14 17:14 | jrojas92
11 | 1008 | Chilled Water | NALCO | 486 | 8.6 | 70 | 0 | 5.5 | 0 | 5.94 |  | 29920.86 |  |  |  |  | jrojas92 | 2015-05-14 18:02 | 2015-11-14 18:05 | jrojas92
12 | 1008 | Chilled Water | NALCO | 482 | 8.4 | 70.2 | 0 | 5.3 | 0 | 5.32 |  | 29920.86 |  |  |  |  | jrojas92 | 2015-04-24 18:43 | 2015-11-14 18:45 | jrojas92
13 | 1111 | Process Chilled Water | NALCO | 3325 | 9.4 | 10.4 | 640 |  |  | 0.3 | 100 |  |  |  |  | ​Approx. Glycol​ 0-10F | reedhea | 2017-03-31 09:42 | 2017-04-10 09:43 | Jay Dahlstrom
14 | 1164 | Process Chilled Water | NALCO | 159 | 7.9 | 0 | 0 | 0 | 0.009 | 0.07 |  |  |  |  | No Leaks |  | jrojas92 | 2016-05-16 23:10 | 2016-06-06 23:12 | jrojas92
15 | 1164 | Process Chilled Water | NALCO | 159 | 8 | 0 | 0 | 0 | 0.004 | 0.11 |  |  |  |  | No Leaks |  | jrojas92 | 2016-04-29 21:14 | 2016-06-06 21:16 | jrojas92
16 | 1164 | Process Chilled Water | NALCO | 158 | 8.6 | 0.7 | 0 | 0 | 0.0093 | 0.07 |  |  |  |  | No Leaks |  | jrojas92 | 2016-03-21 17:54 | 2016-05-02 17:55 | jrojas92
17 | 1164 | Process Chilled Water | NALCO | 145 | 8.2 | 0.4 | 0 | 0 | 0.0148 | 0.01 |  |  |  |  | No Leaks |  | jrojas92 | 2015-11-23 14:15 | 2015-12-21 14:16 | jrojas92
18 | 1164 | Process Chilled Water | NALCO | 126 | 8.5 | 1.1 | 0 | 0 | 0.0139 | 0.03 |  |  |  |  | No Leaks |  | jrojas92 | 2015-10-16 14:50 | 2015-11-14 14:52 | jrojas92
19 | 1164 | Process Chilled Water | NALCO | 124 | 8.4 | 4.5 | 0 | 0.3 | 0.0053 | 0.6 |  |  |  |  | No Leaks |  | jrojas92 | 2015-09-28 18:23 | 2015-09-30 18:26 | jrojas92
20 | 1164 | Process Chilled Water | NALCO | 2143 | 8.2 | 34.2 | 800 | 6 | 0.00376 | 0.34 | [6 empty] | jrojas92 | 2015-08-27 15:36 | 2015-08-27 15:36 | Jay Dahlstrom
21 | 1164 | Process Chilled Water | NALCO | 119 | 8.6 | 1.8 | 0 | 0.4 | 0.0027 | [5 empty] | No Leaks |  | jrojas92 | 2015-08-24 16:34 | 2015-11-14 16:35 | jrojas92
22 | 1164 | Process Chilled Water | NALCO | 108 | 8.1 | 0.6 | 0 | 0.6 | 0.0018 | 0.08 |  |  |  |  | No Leaks |  | jrojas92 | 2015-06-19 17:24 | 2015-11-14 17:25 | jrojas92
23 | 1164 | Process Chilled Water | NALCO | 107 | 8.7 | 0.9 | 0 | 0.5 | 0.0142 | 0.09 | [6 empty] | jrojas92 | 2015-05-21 18:15 | 2015-11-14 18:16 | jrojas92
24 | 1164 | Process Chilled Water | NALCO | 98 | 8.9 | 1.6 | 0 | 0.5 | 0.0215 | 0.04 | [6 empty] | jrojas92 | 2015-04-24 18:53 | 2015-11-14 18:54 | jrojas92
25 | 1153 | Chilled Water | NALCO | 886 | 9.6 | 102 | 160 | 1.2 | 0.015 | 6.4 |  |  |  |  | No Leaks | ​ | jrojas92 | 2016-05-22 23:39 | 2016-06-06 23:40 | jrojas92
26 | 1153 | Chilled Water | NALCO | 888 | 9.6 | 103 | 200 | 1.3 | 0.007 | 9.1 |  |  |  |  | No Leaks |  | jrojas92 | 2016-04-29 22:12 | 2016-06-06 22:14 | jrojas92
27 | 1153 | Chilled Water | NALCO | 898 | 9.6 | 42.5 | 200 | 1 | 0.023 | 7.6 |  |  |  |  | No Leaks |  | jrojas92 | 2016-03-25 20:09 | 2016-06-06 20:10 | jrojas92
28 | 1153 | Chilled Water | NALCO | 904 | 9.4 | 58.1 | 200 | 1.1 | 0.0073 | 2.3 |  |  |  |  | No Leaks |  | jrojas92 | 2015-11-23 13:55 | 2015-12-22 13:58 | jrojas92
29 | 1153 | Chilled Water | NALCO | 906 | 9.6 | 23.9 | 200 | 1.1 | 0.0154 | 5.7 |  |  |  |  | No Leaks |  | jrojas92 | 2015-10-16 15:16 | 2015-11-14 15:18 | jrojas92
30 | 1153 | Chilled Water | NALCO | 906 | 9.5 | 35.2 | 200 | 1.2 | 0.0122 | 8.1 |  |  |  |  | No Leaks |  | jrojas92 | 2015-09-29 18:48 | 2015-09-30 18:51 | jrojas92
31 | 1153 | Chilled Water | NALCO | 911 | 9.5 | 107.2 | 240 | 1.4 | 0.0291 | 3.3 |  |  |  |  | No Leaks |  | jrojas92 | 2015-08-26 16:53 | 2015-11-14 16:54 | jrojas92
32 | 1153 | Chilled Water | NALCO | 960 | 9.6 | 112.6 | 240 | 1.7 | 0 | 2.86 | [6 empty] | jrojas92 | 2015-07-16 13:50 | 2015-08-18 13:53 | jrojas92
33 | 1153 | Chilled Water | NALCO | 957 | 9.6 | 111.2 | 240 | 2 | 0.0096 | 2.84 |  |  |  |  | No Leaks |  | jrojas92 | 2015-06-19 17:43 | 2015-11-14 17:44 | jrojas92
34 | 1153 | Chilled Water | NALCO | 960 | 9.7 | 114.8 | 240 | 1.8 | 0 | 8.12 | [6 empty] | jrojas92 | 2015-05-21 18:32 | 2015-11-14 18:33 | jrojas92
35 | 1153 | Chilled Water | NALCO | 980 | 9.6 | 118 | 280 | 2.2 | 0 | 1.2 | [6 empty] | jrojas92 | 2015-04-09 19:07 | 2015-11-14 19:09 | jrojas92
36 | 1153 | Glycol | NALCO | 4790 | 12.1 | 0 | 600 | 0 | 0.21 | 0.31 | [6 empty] | jrojas92 | 2016-05-22 23:42 | 2016-06-06 23:43 | jrojas92
37 | 1153 | Glycol | NALCO | 4842 | 12.1 | 0 | 600 | 0 | 0.232 | 0.24 | [5 empty] | ​30% propylene glycol | jrojas92 | 2016-04-29 22:17 | 2016-06-06 22:19 | jrojas92
38 | 1153 | Glycol | NALCO | 4819 | 12.1 | 0 | 600 | 0 | 0.236 | 0.26 | [5 empty] | ​30% propylene glycol | jrojas92 | 2016-03-25 20:13 | 2016-06-06 20:16 | jrojas92
39 | 1153 | Glycol | NALCO | 4831 | 12.1 | 0 | 720 | 0 | 0.1357 | 0.38 | [6 empty] | jrojas92 | 2015-11-23 14:00 | 2015-12-22 14:02 | jrojas92
40 | 1153 | Glycol | NALCO | 4958 | 12.1 | 0 | 720 | 0 | 0.189 | 0.53 | [6 empty] | jrojas92 | 2015-10-16 15:19 | 2015-11-14 15:21 | jrojas92
41 | 1153 | Glycol | NALCO | 4926 | 12.1 |  | 720 |  | 0.1767 | 0.5 | [6 empty] | jrojas92 | 2015-09-29 19:00 | 2015-09-30 19:01 | jrojas92
42 | 1153 | Glycol | NALCO | 5165 | 12 | 6.6 | 800 | 0 | 0.21 | 0.51 | [6 empty] | jrojas92 | 2015-08-26 16:56 | 2015-11-14 16:57 | jrojas92
43 | 1153 | Glycol | NALCO | 5291 | 12.3 | 14.4 | 840 | 0 | 0.208 | 0.54 | [6 empty] | jrojas92 | 2015-06-19 17:46 | 2015-11-14 17:47 | jrojas92
44 | 1153 | Glycol | NALCO | 5306 | 12.4 | 8.9 | 960 | 0 | 0.192 | 0.77 | [6 empty] | jrojas92 | 2015-05-21 18:35 | 2015-11-14 18:36 | jrojas92
45 | 1153 | Glycol | NALCO | 4830 | 12.3 | 12.6 | 360 | 0 | 0.136 | 0.77 | [6 empty] | jrojas92 | 2015-04-09 19:10 | 2015-11-14 19:11 | jrojas92
46 | 1153 | Source | NALCO | 1286 | 8.4 | 268 | 280 | 6.3 | 0.019 | 1.89 |  |  |  |  | No Leaks |  | jrojas92 | 2016-05-22 23:44 | 2016-06-06 23:45 | jrojas92
47 | 1153 | Source | NALCO | 1289 | 8.4 | 241 | 280 | 6.5 | 0.024 | 1.45 |  |  |  |  | No Leaks |  | jrojas92 | 2016-04-29 22:19 | 2016-06-06 22:22 | jrojas92
48 | 1153 | Source | NALCO | 1288 | 8.5 | 42.3 | 280 | 6 | 0.002 | 1.17 |  |  |  |  | No Leaks |  | jrojas92 | 2016-03-25 20:16 | 2016-06-06 20:19 | jrojas92
49 | 1153 | Source | NALCO | 1286 | 8.5 | 50 | 320 | 6.3 | 0.035 | 1.29 | [6 empty] | jrojas92 | 2015-11-23 14:02 | 2015-12-22 14:04 | jrojas92
50 | 1153 | Source | NALCO | 1290 | 8.8 | 97 | 280 | 6 | 0.0101 | 0.92 | [6 empty] | jrojas92 | 2015-10-16 15:23 | 2015-11-14 15:25 | jrojas92
51 | 1153 | Source | NALCO | 1290 | 8.7 | 120.4 | 320 | 6.3 | 0.0448 | 1.65 | [6 empty] | jrojas92 | 2015-09-28 19:04 | 2015-09-30 19:05 | jrojas92
52 | 1153 | Source | NALCO | 1294 | 9 | 243.5 | 360 | 7.3 | 0.0308 | 2.29 | [6 empty] | jrojas92 | 2015-08-27 15:37 | 2015-08-27 15:38 | Jay Dahlstrom
53 | 1153 | Source | NALCO | 1295 | 8.8 | 255.6 | 360 | 8.2 | 0.0247 | 1.32 | [6 empty] | jrojas92 | 2015-08-26 16:57 | 2015-11-14 16:59 | jrojas92
54 | 1153 | Source | NALCO | 1289 | 9 | 248 | 360 | 6.8 | 0.0257 | 1.54 | [6 empty] | jrojas92 | 2015-06-19 17:47 | 2015-11-14 17:49 | jrojas92
55 | 1153 | Source | NALCO | 1291 | 9 | 232 | 440 | 6.1 | 0.0284 | 1.36 | [6 empty] | jrojas92 | 2015-05-21 18:36 | 2015-11-14 18:37 | jrojas92
56 | 1153 | Source | NALCO | 1284 | 9.1 | 240 | 800 | 5.8 | 0.0458 | 1.2 | [6 empty] | jrojas92 | 2015-04-09 19:11 | 2015-11-14 19:12 | jrojas92
57 | 1200 | Chilled Water | NALCO | 410 | 9.7 | 201 | 0 | 14.9 | 0 | 8.3 |  | 12810.4 |  |  | No Leaks |  | jrojas92 | 2016-05-16 23:03 | 2016-06-06 23:06 | jrojas92
58 | 1200 | Chilled Water | NALCO | 440 | 9.8 | 201 | 0 | 17 | 0.067 | 2.3 |  | 12797 |  |  | No Leaks |  | jrojas92 | 2016-04-26 21:08 | 2016-06-06 21:10 | jrojas92
59 | 1200 | Chilled Water | NALCO | 442 | 9.8 | 103 | 0 | 16 | 0 | 2.4 |  | 12783.6 |  |  | No Leaks |  | jrojas92 | 2016-03-25 17:48 | 2016-05-02 17:50 | jrojas92
60 | 1200 | Chilled Water | NALCO | 465 | 9.8 | 112 | 0 | 17.1 | 0 | 2.28 |  | 12783.6 |  |  | No Leaks |  | jrojas92 | 2015-11-30 14:08 | 2015-12-21 14:10 | jrojas92
61 | 1200 | Chilled Water | NALCO | 474 | 9.5 | 162 | 0 | 16 | 0 | 2.37 |  | 12783.6 |  |  | No Leaks |  | jrojas92 | 2015-10-23 14:33 | 2015-11-14 14:36 | jrojas92
62 | 1200 | Chilled Water | NALCO | 88.6 | 9.2 | 1.7 | 0 | 3.2 | 0 | 0.34 |  | 12756.8 |  |  | No Leaks |  | jrojas92 | 2015-09-28 18:07 | 2015-09-30 18:12 | jrojas92
63 | 1200 | Chilled Water | NALCO | 88.1 | 9.4 | 0.1 | 0 | 2.4 | 0 |  |  | 12756.8 |  |  | No Leaks |  | jrojas92 | 2015-08-24 16:30 | 2015-11-14 16:31 | jrojas92
64 | 1200 | Chilled Water | NALCO | 87 | 9.1 | 1.2 | 40 | 2.8 | 0 | 0.11 |  | 12726 |  |  |  |  | jrojas92 | 2015-07-17 12:43 | 2015-08-18 12:48 | jrojas92
65 | 1200 | Chilled Water | NALCO | 86.4 | 9.1 | 3.8 | 0 | 2.6 | 0.0114 | 1.31 |  | 12756.8 |  |  | No Leaks |  | jrojas92 | 2015-06-19 17:19 | 2015-11-14 17:21 | jrojas92
66 | 1200 | Chilled Water | NALCO | 81 | 9 | 0.5 | 0 | 1.9 | 0 | 0.45 |  | 12756.8 |  |  |  |  | jrojas92 | 2015-05-14 18:11 | 2015-11-14 18:12 | jrojas92
67 | 1200 | Chilled Water | NALCO | 86 | 9.5 | 0.8 | 40 | 2.7 | 0 | 0.02 |  | 12743.4 |  |  |  |  | jrojas92 | 2015-04-24 18:50 | 2015-11-14 18:51 | jrojas92
68 | 1200 | Process Chilled Water | NALCO | 412 | 9.7 | 205 | 0 | 16.7 | 0 | 1.97 | [6 empty] | jrojas92 | 2016-05-16 23:08 | 2016-06-06 23:09 | jrojas92
69 | 1200 | Process Chilled Water | NALCO | 440 | 9.8 | 96 | 0 | 14.6 | 0 | 1.58 | [6 empty] | jrojas92 | 2016-04-26 21:12 | 2016-06-06 21:14 | jrojas92
70 | 1200 | Process Chilled Water | NALCO | 442 | 9.9 | 44 | 0 | 17.1 | 0.0595 | 2.52 | [6 empty] | jrojas92 | 2016-03-25 17:52 | 2016-05-02 17:54 | jrojas92
71 | 1200 | Process Chilled Water | NALCO | 465 | 9.8 | 132 | 0 | 17 | 0 | 2.13 | [6 empty] | jrojas92 | 2015-11-30 14:12 | 2015-12-21 14:13 | jrojas92
72 | 1200 | Process Chilled Water | NALCO | 471 | 9 | 112 | 0 | 17.4 | 0 | 14.2 | [6 empty] | jrojas92 | 2015-10-23 14:44 | 2015-11-14 14:48 | jrojas92
73 | 1200 | Process Chilled Water | NALCO | 88.7 | 9.2 | 2.5 | 0 | 3 | 0 | 0.77 | [6 empty] | jrojas92 | 2015-09-28 18:16 | 2015-09-30 18:18 | jrojas92
74 | 1200 | Process Chilled Water | NALCO | 87 | 9.2 | 0.9 | 40 | 2.8 | 0.0019 | 0.1 | [6 empty] | jrojas92 | 2015-08-27 15:31 | 2015-08-27 15:33 | Jay Dahlstrom
75 | 1200 | Process Chilled Water | NALCO | 88 | 9.3 | 0.5 | 0 | 3.2 | 0 | [7 empty] | jrojas92 | 2015-08-24 16:33 | 2015-11-14 16:34 | jrojas92
76 | 1200 | Process Chilled Water | NALCO | 86.3 | 9 | 0.2 | 0 | 2.7 | 0 | 0.41 | [6 empty] | jrojas92 | 2015-06-19 17:22 | 2015-11-14 17:23 | jrojas92
77 | 1200 | Process Chilled Water | NALCO | 81 | 9 | 0.3 | 40 | 2.2 | 0 | 0.16 | [6 empty] | jrojas92 | 2015-05-14 18:14 | 2015-11-14 18:15 | jrojas92
78 | 1200 | Process Chilled Water | NALCO | 86 | 9.3 | 0.4 | 0 | 2.9 | 0 | 0.05 | [6 empty] | jrojas92 | 2015-04-24 18:52 | 2015-11-14 18:53 | jrojas92
79 | 1314 | Process Chilled Water | NALCO | 670 | 4.9 | 0 | 0 | 0 |  | 180 | [5 empty] | Recommendations:​ Flush loop from every available point to clear fouling from system. Cycle through each CHW pump every week. Add biocide & cleaner to clean loop up & re-passivate. Charge loop with Glycol and Inhibitor. | bschmidt | 2017-01-03 15:43 | 2017-02-08 15:48 | bschmidt
80 | 5980 | Chilled Water | NALCO | 1157 | 10.4 | 2.1 | 200 | 6.4 | 0.039 | 9.81 |  | 281.4 |  |  | No Leaks |  | jrojas92 | 2016-05-18 23:18 | 2016-06-06 23:20 | jrojas92
81 | 5980 | Chilled Water | NALCO | 1152 | 10.4 | 2 | 200 | 6 | 0.107 | 7.7 |  | 281.4 |  |  | No Leaks |  | jrojas92 | 2016-04-25 21:24 | 2016-06-06 21:25 | jrojas92
82 | 5980 | Chilled Water | NALCO | 1157 | 10.4 | 4.6 | 200 | 6.1 | 0.0544 | 6 |  | 281.4 |  |  | No Leaks |  | jrojas92 | 2016-03-25 18:03 | 2016-05-02 18:05 | jrojas92
83 | 5980 | Chilled Water | NALCO | 1154 | 10.3 | 4.5 | 240 | 6 | 0.065 | 6.4 |  | 281.4 |  |  | No Leaks |  | jrojas92 | 2015-11-24 14:20 | 2015-12-21 14:21 | jrojas92
84 | 5980 | Chilled Water | NALCO | 1164 | 10.4 | 4.8 | 240 | 6.2 |  | 7 |  | 2100 |  |  | No Leaks | ​ | jrojas92 | 2015-10-30 14:57 | 2015-11-14 14:59 | jrojas92
85 | 5980 | Chilled Water | NALCO | 1165 | 10.3 | 6.1 | 200 | 6.3 | 0.0526 | 10.5 |  | 281.4 |  |  | No Leaks | ​ | jrojas92 | 2015-09-24 18:32 | 2015-09-30 18:36 | jrojas92
86 | 5980 | Chilled Water | NALCO | 1175 | 10.3 | 0.9 | 240 | 6.3 | 0.0343 | 8.25 |  | 281.4 |  |  | No Leaks |  | jrojas92 | 2015-08-24 16:40 | 2015-11-14 16:42 | jrojas92
87 | 5980 | Chilled Water | NALCO | 1198 | 10.3 | 7.1 | 240 | 5.9 | 0.05 | 6.13 |  | 281 |  |  |  |  | jrojas92 | 2015-07-16 13:15 | 2015-08-18 13:19 | jrojas92
88 | 5980 | Chilled Water | NALCO | 1195 | 10.4 | 5.6 | 240 | 6.8 | 0.0373 | 7.52 |  | 281.4 |  |  | No Leaks |  | jrojas92 | 2015-06-22 17:29 | 2015-11-14 17:31 | jrojas92
89 | 5980 | Chilled Water | NALCO | 1198 | 10.4 | 14.2 | 240 | 7.1 | 0.0456 | 6.5 |  | 281.4 |  |  |  |  | jrojas92 | 2015-05-21 18:22 | 2015-11-14 18:23 | jrojas92
90 | 5980 | Chilled Water | NALCO | 1190 | 10.3 | 5.1 | 240 | 3.2 | 0.0162 | 5.6 |  | 281.4 |  |  |  |  | jrojas92 | 2015-04-08 18:59 | 2015-11-14 19:00 | jrojas92
91 | 1420 | Chilled Water | NALCO | 325 | 10.1 | 1.4 | 40 | 0 | 0.03 | 0.81 |  |  |  |  | No Leaks |  | jrojas92 | 2016-05-18 23:29 | 2016-06-06 23:32 | jrojas92
92 | 1420 | Chilled Water | NALCO | 323 | 10.1 | 1.3 | 40 | 0.5 | 0.029 | 0.56 |  |  |  |  | No Leaks |  | jrojas92 | 2016-04-25 22:01 | 2016-06-06 22:04 | jrojas92
93 | 1420 | Chilled Water | NALCO | 323 | 10.1 | 1.9 | 40 | 0.4 | 0.024 | 0.52 |  |  |  |  | No Leaks |  | jrojas92 | 2016-03-25 19:58 | 2016-06-06 20:00 | jrojas92
94 | 1420 | Chilled Water | NALCO | 324 | 9.9 | 2.9 | 40 | 0 | 0.1031 | 0.52 |  |  |  |  | No Leaks |  | jrojas92 | 2015-11-24 14:27 | 2015-12-21 14:28 | jrojas92
95 | 1420 | Chilled Water | NALCO | 327 | 9.9 | 0.8 | 40 | 0 | 0.21 | 0.51 |  |  |  |  | No Leaks |  | jrojas92 | 2015-10-30 15:08 | 2015-11-14 15:10 | jrojas92
96 | 1420 | Chilled Water | NALCO | 326 | 9.9 | 1.4 | 40 | 0.3 | 0.0146 | 0.7 |  |  |  |  | No Leaks |  | jrojas92 | 2015-09-24 18:44 | 2015-09-30 18:45 | jrojas92
97 | 1420 | Chilled Water | NALCO | 329 | 10 | 1.4 | 40 | 0.5 | 0.0379 | 0.65 |  |  |  |  | No Leaks |  | jrojas92 | 2015-08-26 16:46 | 2015-11-14 16:47 | jrojas92
98 | 1420 | Chilled Water | NALCO | 327 | 9.9 | 3.1 | 40 | 0.3 | 0.0189 | 0.56 | [6 empty] | jrojas92 | 2015-07-16 13:30 | 2015-08-18 13:33 | jrojas92
99 | 1420 | Chilled Water | NALCO | 325 | 9.9 | 1.7 | 40 | 0.4 | 0.0178 | 0.63 |  |  |  |  | No Leaks |  | jrojas92 | 2015-06-22 17:37 | 2015-11-14 17:38 | jrojas92
100 | 1420 | Chilled Water | NALCO | 327 | 10 | 4.7 | 40 | 0.9 | 0.0098 | 0.79 | [6 empty] | jrojas92 | 2015-05-21 18:27 | 2015-11-14 18:28 | jrojas92
101 | 1420 | Chilled Water | NALCO | 328 | 10 | 1.4 | 40 | 0.4 | 0.0134 | 0.39 | [6 empty] | jrojas92 | 2015-04-08 19:04 | 2015-11-14 19:05 | jrojas92
102 | 1008 | Heating Hot Water | NALCO | 1046 | 9.7 |  | 240 |  |  | 1.8 | [5 empty] | ​ | reedhea | 2017-03-31 09:00 | 2017-04-10 09:03 | Jay Dahlstrom
103 | 1008 | Heating Hot Water | NALCO | 1026 | 10.7 |  | 200 | 13.5 | 0.013 | 0.06 |  | 26140.586 |  |  | No Leaks |  | jrojas92 | 2016-05-16 22:57 | 2016-06-06 22:59 | jrojas92
104 | 1008 | Heating Hot Water | NALCO | 1056 | 10.7 |  | 240 | 13.7 | 0.018 | 0.12 |  | 26095.16 |  |  | No Leaks | ​​ | jrojas92 | 2016-04-18 | 2016-06-06 21:04 | jrojas92
105 | 1008 | Heating Hot Water | NALCO | 1116 | 10.6 |  | 240 | 16.3 | 0.036 | 0.14 |  | 26063 |  |  | No Leaks |  | jrojas92 | 2016-03-25 22:14 | 2016-04-27 22:18 | jrojas92
106 | 1008 | Heating Hot Water | NALCO | 1120 | 10.6 |  | 280 | 15.8 | 0.0178 | 0.05 |  | 26049.6 |  |  | No Leaks |  | jrojas92 | 2015-11-24 14:01 | 2015-12-21 14:03 | jrojas92
107 | 1008 | Heating Hot Water | NALCO | 1123 | 10.2 |  | 280 | 17.9 | 0.0082 | 0.09 |  | 26049.6 |  |  | No Leaks | ​​ | jrojas92 | 2015-10-23 14:23 | 2015-11-14 14:26 | jrojas92
108 | 1008 | Heating Hot Water | NALCO | 440 | 10.4 |  | 80 | 4.9 | 0.0093 | 0.06 |  | 26048.26 |  |  | No Leaks |  | jrojas92 | 2015-09-28 17:38 | 2015-09-30 17:46 | jrojas92
109 | 1008 | Heating Hot Water | NALCO | 458 | 10.4 |  | 80 | 5.4 | 0.0036 |  |  | 26042.9 |  |  | No Leaks |  | jrojas92 | 2015-08-24 16:24 | 2015-11-14 16:26 | jrojas92
110 | 1008 | Heating Hot Water | NALCO | 452 | 10.3 |  | 80 | 5.1 | 0.0148 | 0.46 |  | 25979 |  |  |  |  | jrojas92 | 2015-07-17 12:18 | 2015-08-18 12:23 | jrojas92
111 | 1008 | Heating Hot Water | NALCO | 446 | 10.4 |  | 80 | 5 | 0.0091 | 0.17 |  | 26040.22 |  |  | No Leaks |  | jrojas92 | 2015-06-19 17:14 | 2015-11-14 17:15 | jrojas92
112 | 1008 | Heating Hot Water | NALCO | 455 | 10.5 |  | 80 | 6.4 | 0.0104 | 0.04 |  | 26029.5 |  |  |  |  | jrojas92 | 2015-05-14 18:05 | 2015-11-14 18:07 | jrojas92
113 | 1008 | Heating Hot Water | NALCO | 469 | 10.4 |  | 80 | 7 | 0.0155 | 0.07 |  | 26021.46 |  |  |  |  | jrojas92 | 2015-04-24 18:45 | 2015-11-14 18:47 | jrojas92
114 | 1164 | Heating Hot Water | NALCO | 69 | 7.8 |  | 0 | 0 | 0.01 | 0.16 | [6 empty] | jrojas92 | 2016-05-16 23:12 | 2016-06-06 23:14 | jrojas92
115 | 1164 | Heating Hot Water | NALCO | 69 | 7.9 |  | 0 | 0.1 | 0.055 | 0.24 | [6 empty] | jrojas92 | 2016-04-29 21:18 | 2016-06-06 21:20 | jrojas92
116 | 1164 | Heating Hot Water | NALCO | 69.8 | 8.2 |  | 0 | 0 | 0.0413 | 0.45 | [6 empty] | jrojas92 | 2016-03-21 17:56 | 2016-05-02 17:57 | jrojas92
117 | 1164 | Heating Hot Water | NALCO | 69.1 | 8.5 |  | 0 | 0.3 | 0.0779 | 0.09 | [6 empty] | jrojas92 | 2015-11-23 14:13 | 2015-12-21 14:14 | jrojas92
118 | 1164 | Heating Hot Water | NALCO | 69 | 8.5 |  | 0 | 0.1 | 0.0167 | 0.15 | [6 empty] | jrojas92 | 2015-10-16 14:49 | 2015-11-14 14:50 | jrojas92
119 | 1164 | Heating Hot Water | NALCO | 68.9 | 8.5 |  | 0 | 0 | 0.0146 | 0.11 | [6 empty] | jrojas92 | 2015-09-28 18:20 | 2015-09-30 18:22 | jrojas92
120 | 1164 | Heating Hot Water | NALCO | 68.4 | 8.6 |  | 0 | 0 | 0.0181 | [6 empty] | ​ | jrojas92 | 2015-08-24 16:35 | 2015-11-14 16:37 | jrojas92
121 | 1164 | Heating Hot Water | NALCO | 67 | 8.7 |  | 40 | 0.6 | 0.0225 | 0.11 | [6 empty] | jrojas92 | 2015-07-16 13:02 | 2015-08-18 13:05 | jrojas92
122 | 1164 | Heating Hot Water | NALCO | 67.2 | 8.3 |  | 0 | 0.2 | 0.0217 | 0.27 | [6 empty] | jrojas92 | 2015-06-19 17:25 | 2015-11-14 17:26 | jrojas92
123 | 1164 | Heating Hot Water | NALCO | 66.4 | 8.5 |  | 0 | 0.3 | 0.0249 | 0.28 | [6 empty] | jrojas92 | 2015-05-21 18:16 | 2015-11-14 18:18 | jrojas92
124 | 1164 | Heating Hot Water | NALCO | 67 | 8.6 |  | 0 | 0.2 | 0.0396 | 0.36 | [6 empty] | jrojas92 | 2015-04-24 18:55 | 2015-11-14 18:56 | jrojas92
125 | 1153 | Heating Hot Water | NALCO | 900 | 9.7 |  | 160 | 0 | 0.088 | 4.9 |  |  |  |  | No Leaks |  | jrojas92 | 2016-05-22 23:41 | 2016-06-06 23:42 | jrojas92
126 | 1153 | Heating Hot Water | NALCO | 903 | 9.7 |  | 160 | 0 | 0.151 | 5.3 |  |  |  |  | No Leaks |  | jrojas92 | 2016-04-29 22:14 | 2016-06-06 22:17 | jrojas92
127 | 1153 | Heating Hot Water | NALCO | 910 | 9.7 |  | 160 | 0 | 0.139 | 4.45 |  |  |  |  | No Leaks | ​ | jrojas92 | 2016-03-25 20:11 | 2016-06-06 20:13 | jrojas92
128 | 1153 | Heating Hot Water | NALCO | 920 | 9.5 |  | 200 | 0.5 | 0.0985 | 2.01 |  |  |  |  | No Leaks |  | jrojas92 | 2015-11-23 13:58 | 2015-12-22 14:00 | jrojas92
129 | 1153 | Heating Hot Water | NALCO | 952 | 9.6 |  | 200 | 0.2 | 0.0522 | 1.75 |  |  |  |  | No Leaks |  | jrojas92 | 2015-10-16 15:18 | 2015-11-14 15:19 | jrojas92
130 | 1153 | Heating Hot Water | NALCO | 956 | 9.6 |  | 160 | 0.3 | 0.0215 | 1.78 |  |  |  |  | No Leaks |  | jrojas92 | 2015-09-29 19:01 | 2015-09-30 19:03 | jrojas92
131 | 1153 | Heating Hot Water | NALCO | 958 | 9.6 |  | 240 | 0.7 | 0.0576 | 2.72 |  |  |  |  | No Leaks |  | jrojas92 | 2015-08-26 16:54 | 2015-11-14 16:56 | jrojas92
132 | 1153 | Heating Hot Water | NALCO | 959 | 9.6 |  | 240 | 0.9 | 0.0199 | 1.89 | [5 empty] | ​ | jrojas92 | 2015-07-16 13:54 | 2015-08-18 13:56 | jrojas92
133 | 1153 | Heating Hot Water | NALCO | 955 | 9.6 |  | 240 | 0.7 | 0.0484 | 0.88 |  |  |  |  | No Leaks |  | jrojas92 | 2015-06-19 17:44 | 2015-11-14 17:46 | jrojas92
134 | 1153 | Heating Hot Water | NALCO | 957 | 9.8 |  | 240 | 0.6 | 0.0009 | 1.89 | [6 empty] | jrojas92 | 2015-05-21 18:33 | 2015-11-14 18:34 | jrojas92
135 | 1153 | Heating Hot Water | NALCO | 956 | 9.8 |  | 240 | 0 | 0.0155 | 2 | [6 empty] | jrojas92 | 2015-04-09 19:09 | 2015-11-14 19:10 | jrojas92
136 | 1200 | Heating Hot Water | NALCO | 163 | 8.5 |  | 0 | 0 | 0.013 | 0.76 |  |  |  |  | No Leaks |  | jrojas92 | 2016-05-16 23:06 | 2016-06-06 23:08 | jrojas92
137 | 1200 | Heating Hot Water | NALCO | 160 | 8.5 |  | 0 | 0 | 0.035 | 0.28 |  |  |  |  | No Leaks |  | jrojas92 | 2016-04-26 21:10 | 2016-06-06 21:12 | jrojas92
138 | 1200 | Heating Hot Water | NALCO | 156 | 8.6 |  | 0 | 0 | 0.0112 | 0.25 |  |  |  |  | No Leaks |  | jrojas92 | 2016-03-25 17:50 | 2016-05-02 17:52 | jrojas92
139 | 1200 | Heating Hot Water | NALCO | 101 | 8.6 |  | 0 | 0 | 0.0091 | 0.57 |  |  |  |  | No Leaks |  | jrojas92 | 2015-11-30 14:10 | 2015-12-21 14:11 | jrojas92
140 | 1200 | Heating Hot Water | NALCO | 84.8 | 8.9 |  | 0 | 0 | 0.0323 | 0.72 |  |  |  |  | No Leaks |  | jrojas92 | 2015-10-23 14:42 | 2015-11-14 14:44 | jrojas92
141 | 1200 | Heating Hot Water | NALCO | 77.1 | 8.9 |  | 0 | 0 | 0.0161 | 0.64 |  |  |  |  | No Leaks |  | jrojas92 | 2015-09-28 18:12 | 2015-09-30 18:15 | jrojas92
142 | 1200 | Heating Hot Water | NALCO | 74.8 | 8.7 |  | 0 | 0 | 0.0433 | [5 empty] | No Leaks |  | jrojas92 | 2015-08-24 16:31 | 2015-11-14 16:33 | jrojas92
143 | 1200 | Heating Hot Water | NALCO | 70 | 8.6 |  | 40 | 0 | 0.0394 | 0.43 | [5 empty] | ​​ | jrojas92 | 2015-07-17 12:49 | 2015-08-18 12:53 | jrojas92
144 | 1200 | Heating Hot Water | NALCO | 67.5 | 8.5 |  | 0 | 0 | 0.063 | 1.52 |  |  |  |  | No Leaks |  | jrojas92 | 2015-06-19 17:21 | 2015-11-14 17:22 | jrojas92
145 | 1200 | Heating Hot Water | NALCO | 69 | 8.5 |  | 0 | 0 | 0.0642 | 0.51 | [6 empty] | jrojas92 | 2015-05-14 18:12 | 2015-11-14 18:14 | jrojas92
146 | 1200 | Heating Hot Water | NALCO | 68 | 9 |  | 0 | 0.7 | 0.0534 | 0.5 |  |  |  |  | No Leaks |  | jrojas92 | 2015-04-24 18:51 | 2015-11-14 18:52 | jrojas92
147 | 5980 | Heating Hot Water | NALCO | 189 | 8.7 |  | 0 | 3.1 | 0 | 0.45 |  | 28568.8 |  |  | No Leaks |  | jrojas92 | 2016-05-18 23:20 | 2016-06-06 23:23 | jrojas92
148 | 5980 | Heating Hot Water | NALCO | 190 | 8.7 |  | 0 | 3.9 | 0.003 | 0.61 |  | 28568.8 |  |  | No Leaks |  | jrojas92 | 2016-04-25 21:25 | 2016-06-06 21:26 | jrojas92
149 | 5980 | Heating Hot Water | NALCO | 205 | 8.7 |  | 0 | 3.8 | 0 | 0.5 |  | 28568.8 |  |  | No Leaks |  | jrojas92 | 2016-03-25 18:05 | 2016-05-02 18:06 | jrojas92
150 | 5980 | Heating Hot Water | NALCO | 213 | 9 |  | 0 | 3.8 | 0.0091 | 0.4 |  | 28568.8 |  |  | No Leaks |  | jrojas92 | 2015-11-24 14:21 | 2015-12-21 14:23 | jrojas92
151 | 5980 | Heating Hot Water | NALCO | 215 | 9.1 |  | 0 | 3.3 |  | 0.59 |  | 28568.8 |  |  | No Leaks |  | jrojas92 | 2015-10-30 14:59 | 2015-11-14 15:04 | jrojas92
152 | 5980 | Heating Hot Water | NALCO | 216 | 9 |  | 0 | 3 | 0 | 0.75 |  | 28568.8 |  |  | No Leaks |  | jrojas92 | 2015-09-24 18:37 | 2015-09-30 18:38 | jrojas92
153 | 5980 | Heating Hot Water | NALCO | 221 | 9 |  | 0 | 3.4 | 0 | 0.67 |  | 28568.8 |  |  | No Leaks |  | jrojas92 | 2015-08-24 16:42 | 2015-11-14 16:43 | jrojas92
154 | 5980 | Heating Hot Water | NALCO | 225 | 9.1 |  | 40 | 3.9 | 0 | 0.78 |  | 28501 |  |  |  |  | jrojas92 | 2015-07-16 13:19 | 2015-08-18 13:23 | jrojas92
155 | 5980 | Heating Hot Water | NALCO | 227 | 9.1 |  | 0 | 3.9 | 0 | 0.76 |  | 28568.8 |  |  | No Leaks |  | jrojas92 | 2015-06-22 17:31 | 2015-11-14 17:33 | jrojas92
156 | 5980 | Heating Hot Water | NALCO | 262 | 9.1 |  | 0 | 4.5 | 0 | 0.74 |  | 28568.8 |  |  |  |  | jrojas92 | 2015-05-21 18:23 | 2015-11-14 18:24 | jrojas92
157 | 5980 | Heating Hot Water | NALCO | 239 | 9.1 |  | 0 | 2.8 | 0 | 0.7 |  | 28568.8 |  |  |  |  | jrojas92 | 2015-04-08 19:00 | 2015-11-14 19:01 | jrojas92
158 | 1420 | Heating Hot Water | NALCO | 1891 | 11.1 |  | 440 | 0.2 | 0.57 | 0.28 |  |  |  |  | No Leaks |  | jrojas92 | 2016-05-18 23:33 | 2016-06-06 23:34 | jrojas92
159 | 1420 | Heating Hot Water | NALCO | 1878 | 11.1 |  | 440 | 0.1 | 0.771 | 0.15 |  |  |  |  | No Leaks |  | jrojas92 | 2016-04-25 22:04 | 2016-06-06 22:07 | jrojas92
160 | 1420 | Heating Hot Water | NALCO | 1906 | 11 |  | 440 | 0.5 | 0.899 | 0.21 |  |  |  |  | No Leaks |  | jrojas92 | 2016-03-25 20:01 | 2016-06-06 20:02 | jrojas92
161 | 1420 | Heating Hot Water | NALCO | 1889 | 11.1 |  | 440 | 0 | 0.8406 | 0.21 |  |  |  |  | No Leaks |  | jrojas92 | 2015-11-24 14:28 | 2015-12-21 14:29 | jrojas92
162 | 1420 | Heating Hot Water | NALCO | 1888 | 11 |  | 480 | 0 | 0.21 | 0.19 |  |  |  |  | No Leaks |  | jrojas92 | 2015-10-30 15:10 | 2015-11-14 15:12 | jrojas92
163 | 1420 | Heating Hot Water | NALCO | 1867 | 10.9 |  | 400 | 0 | 0.3598 | 0.26 | [6 empty] | jrojas92 | 2015-09-24 18:45 | 2015-09-30 18:47 | jrojas92
164 | 1420 | Heating Hot Water | NALCO | 1897 | 11 |  | 560 | 0.7 | 0.117 | 0.25 |  |  |  |  | No Leaks |  | jrojas92 | 2015-08-26 16:48 | 2015-11-14 16:49 | jrojas92
165 | 1420 | Heating Hot Water | NALCO | 1876 | 10.9 |  | 480 | 0.1 | 0.361 | 0.28 | [5 empty] | ​​ | jrojas92 | 2015-07-16 13:33 | 2015-08-18 13:36 | jrojas92
166 | 1420 | Heating Hot Water | NALCO | 1878 | 11 |  | 560 | 0.6 | 0.3 | 0.23 |  |  |  |  | No Leaks |  | jrojas92 | 2015-06-22 17:38 | 2015-11-14 17:39 | jrojas92
167 | 1420 | Heating Hot Water | NALCO | 1893 | 11.2 |  | 520 | 0 | 0.365 | 0.23 | [6 empty] | jrojas92 | 2015-05-21 18:28 | 2015-11-14 18:29 | jrojas92
168 | 1420 | Heating Hot Water | NALCO | 1888 | 11.1 |  | 560 | 0 | 0.0721 | 0.28 | [6 empty] | jrojas92 | 2015-04-08 19:05 | 2015-11-14 19:06 | jrojas92